## IP
GI Pekalongan
| F87L / F87T | F67 / F51 | BCU | F501 | F502
Pemalang1 | 198.120.0.27 | 198.120.0.28 | 198.120.0.29
Pemalang2 | 198.120.0.30 | 198.120.0.31 | 198.120.0.32
Pekalongan1 | 198.120.0.21 | 198.120.0.22 | 198.120.0.23
Pekalongan2 | 198.120.0.24 | 198.120.0.25 | 198.120.0.26
Kopel |  | 198.120.0.33 | 198.120.0.34
Trafo1 | 198.120.0.37 |  | 198.120.0.40 | 198.120.0.38 | 198.120.0.39

## PEMALANG 1
No | Gardu Induk | Bay | IED | HMI | POINT | DATABASE |  | Type
1 | Comal | Pemalang 1 | D29 | F87L FAIL | BCU_F87l_FAIL | f87lfail | D29CTRL/GGIO17.Ind8.stVal | Boolean | ADD `f87lfail` CHAR(10) NOT NULL AFTER `bay`, | ''D29CTRL/GGIO17.Ind8.stVal'', //f87lfail | f87lfail=?,
2 | Comal | Pemalang 1 | D29 | F87L ALARM | BCU_F87l_ALARM | f87lalarm | D29CTRL/GGIO18.Ind1.stVal | Boolean | ADD `f87lalarm` CHAR(10) NOT NULL AFTER `f87lfail`, | ''D29CTRL/GGIO18.Ind1.stVal'', //f87lalarm | f87lalarm=?,
3 | Comal | Pemalang 1 | D29 | F50 FAIL | BCU_F50_FAIL | f50fail | D29CTRL/GGIO18.Ind4.stVal | Boolean | ADD `f50fail` CHAR(10) NOT NULL AFTER `f87lalarm`, | ''D29CTRL/GGIO18.Ind4.stVal'', //f50fail | f50fail=?,
4 | Comal | Pemalang 1 | D29 | F50 ALARM | BCU_F50_ALARM | f50alarm | D29CTRL/GGIO18.Ind5.stVal | Boolean | ADD `f50alarm` CHAR(10) NOT NULL AFTER `f50fail`, | ''D29CTRL/GGIO18.Ind5.stVal'', //f50alarm | f50alarm=?,
7 | Comal | Pemalang 1 | D29 | MCB AC | BCU_MCB_AC | mcbac | D29CTRL/GGIO17.Ind7.stVal | Boolean | ADD `mcbac` CHAR(10) NOT NULL AFTER `f50alarm`, | ''D29CTRL/GGIO17.Ind7.stVal'', //mcbac | mcbac=?,
8 | Comal | Pemalang 1 | D29 | AUX DC SUPPLY | BCU_MCB_AUX_DC_SUPPLY | auxdcsupply | D29CTRL/GGIO19.Ind4.stVal | Boolean | ADD `auxdcsupply` CHAR(10) NOT NULL AFTER `mcbac`, | ''D29CTRL/GGIO19.Ind4.stVal'', //auxdcsupply | auxdcsupply=?,
10 | Comal | Pemalang 1 | D29 | Q21 AND Q22 CLOSE | BCU_Q21_AND_Q22_CLOSE | q21q22close | D29CTRL/GGIO19.Ind7.stVal | Boolean | ADD `q21q22close` CHAR(10) NOT NULL AFTER `auxdcsupply`, | ''D29CTRL/GGIO19.Ind7.stVal'', //q21q22close | q21q22close=?,
11 | Comal | Pemalang 1 | D29 | CB SRING CHARGE FAIL | BCU_CB_SPRING_CHRG_FAIL | cbsringchargefail | D29CTRL/GGIO20.Ind6.stVal | Boolean | ADD `cbsringchargefail` CHAR(10) NOT NULL AFTER `q21q22close`, | ''D29CTRL/GGIO20.Ind6.stVal'', //cbsringchargefail | cbsringchargefail=?,
13 | Comal | Pemalang 1 | D29 | CB MOTOR MCB TRIP | BCU_CB_MOTOR_MCB_TRIP | cbmotormcbtrip | D29CTRL/GGIO20.Ind7.stVal | Boolean | ADD `cbmotormcbtrip` CHAR(10) NOT NULL AFTER `cbsringchargefail`, | ''D29CTRL/GGIO20.Ind7.stVal'', //cbmotormcbtrip | cbmotormcbtrip=?,
14 | Comal | Pemalang 1 | D29 | CB PHS R CLOSE SPRING UNCHARGE | BCU_CB_PHS.R_CLS_SPRING_UNCHRG | springfailR | D29CTRL/GGIO20.Ind8.stVal | Boolean | ADD `springfailR` CHAR(10) NOT NULL AFTER `cbmotormcbtrip`, | ''D29CTRL/GGIO20.Ind8.stVal'', //springfailR | springfailR=?,
15 | Comal | Pemalang 1 | D29 | CB PHS S CLOSE SPRING UNCHARGE | BCU_CB_PHS.S_CLS_SPRING_UNCHRG | springfailS | D29CTRL/GGIO21.Ind1.stVal | Boolean | ADD `springfailS` CHAR(10) NOT NULL AFTER `springfailR`, | ''D29CTRL/GGIO21.Ind1.stVal'', //springfailS | springfailS=?,
16 | Comal | Pemalang 1 | D29 | CB PHS T CLOSE SPRING UNCHARGE | BCU_CB_PHS.T_CLS_SPRING_UNCHRG | springfailT | D29CTRL/GGIO21.Ind2.stVal | Boolean | ADD `springfailT` CHAR(10) NOT NULL AFTER `springfailS`, | ''D29CTRL/GGIO21.Ind2.stVal'', //springfailT | springfailT=?,
17 | Comal | Pemalang 1 | D29 | SF6 STAGE 2 BLOCK | BCU_SF6 STAGE 2 BLOK | sf6block | D29CTRL/GGIO21.Ind3.stVal | Boolean | ADD `sf6block` CHAR(10) NOT NULL AFTER `springfailT`, | ''D29CTRL/GGIO21.Ind3.stVal'', //sf6block | sf6block=?,
18 | Comal | Pemalang 1 | D29 | TRIP CIRCUIT 2 BLOCKED | BCU_TRIP_CIRCUIT_2_BLOCKED | tcs2block | D29CTRL/GGIO21.Ind4.stVal | Boolean | ADD `tcs2block` CHAR(10) NOT NULL AFTER `sf6block`, | ''D29CTRL/GGIO21.Ind4.stVal'', //tcs2block | tcs2block=?,
19 | Comal | Pemalang 1 | D29 | SF6 STAGE 1 ALARM | BCU_SF6 STAGE 1 ALARM | sf6alarm | D29CTRL/GGIO21.Ind5.stVal | Boolean | ADD `sf6alarm` CHAR(10) NOT NULL AFTER `tcs2block`, | ''D29CTRL/GGIO21.Ind5.stVal'', //sf6alarm | sf6alarm=?,
20 | Comal | Pemalang 1 | D29 | CB ALARM AC CIRCUIT | BCU_CB_ALARM_AC_CIRCUIT | cbalarmac | D29CTRL/GGIO22.Ind1.stVal | Boolean | ADD `cbalarmac` CHAR(10) NOT NULL AFTER `sf6alarm`, | ''D29CTRL/GGIO22.Ind1.stVal'', //cbalarmac | cbalarmac=?,
21 | Comal | Pemalang 1 | D29 | CB POLE DISCREPANCY | BCU_CB POLE DISCREPANCY | poledis | D29CTRL/GGIO22.Ind3.stVal | Boolean | ADD `poledis` CHAR(10) NOT NULL AFTER `cbalarmac`, | ''D29CTRL/GGIO22.Ind3.stVal'', //poledis | poledis=?,
22 | Comal | Pemalang 1 | D29 | DS Q21 MOTOR MCB TRIP | BCU_DS_Q21_MOTOR_MCB_TRIP | q21motor | D29CTRL/GGIO22.Ind8.stVal | Boolean | ADD `q21motor` CHAR(10) NOT NULL AFTER `poledis`, | ''D29CTRL/GGIO22.Ind8.stVal'', //q21motor | q21motor=?,
24 | Comal | Pemalang 1 | D29 | DS Q21 CONTROL MCB TRIP | BCU_DS_Q21_CONTROL_MCB_TRIP | q21control | D29CTRL/GGIO23.Ind1.stVal | Boolean | ADD `q21control` CHAR(10) NOT NULL AFTER `q21motor`, | ''D29CTRL/GGIO23.Ind1.stVal'', //q21control | q21control=?,
25 | Comal | Pemalang 1 | D29 | DS Q22 MOTOR MCB TRIP | BCU_DS_Q22_MOTOR_MCB_TRIP | q22motor | D29CTRL/GGIO23.Ind7.stVal | Boolean | ADD `q22motor` CHAR(10) NOT NULL AFTER `q21control`, | ''D29CTRL/GGIO23.Ind7.stVal'', //q22motor | q22motor=?,
26 | Comal | Pemalang 1 | D29 | DS Q22 CONTROL MCB TRIP | BCU_DS_Q22_CONTROL_MCB_TRIP | q22control | D29CTRL/GGIO23.Ind8.stVal | Boolean | ADD `q22control` CHAR(10) NOT NULL AFTER `q22motor`, | ''D29CTRL/GGIO23.Ind8.stVal'', //q22control | q22control=?,
27 | Comal | Pemalang 1 | D29 | DS Q28 MOTOR MCB TRIP | BCU_DS_Q28_MOTOR_MCB_TRIP | q28motor | D29CTRL/GGIO25.Ind1.stVal | Boolean | ADD `q28motor` CHAR(10) NOT NULL AFTER `q22control`, | ''D29CTRL/GGIO25.Ind1.stVal'', //q28motor | q28motor=?,
28 | Comal | Pemalang 1 | D29 | DS Q28 CONTROL MCB TRIP | BCU_DS_Q28_CONTROL_MCB_TRIP | q28control | D29CTRL/GGIO25.Ind2.stVal | Boolean | ADD `q28control` CHAR(10) NOT NULL AFTER `q28motor`, | ''D29CTRL/GGIO25.Ind2.stVal'', //q28control | q28control=?,
29 | Comal | Pemalang 1 | D29 | TCS 1 FAIL PHS R | BCU_TCS_1_FAIL_PHS.R | tcs1r | D29CTRL/GGIO25.Ind8.stVal | Boolean | ADD `tcs1r` CHAR(10) NOT NULL AFTER `q28control`, | ''D29CTRL/GGIO25.Ind8.stVal'', //tcs1r | tcs1r=?,
30 | Comal | Pemalang 1 | D29 | TCS 1 FAIL PHS S | BCU_TCS_1_FAIL_PHS.S | tcs1s | D29CTRL/GGIO26.Ind2.stVal | Boolean | ADD `tcs1s` CHAR(10) NOT NULL AFTER `tcs1r`, | ''D29CTRL/GGIO26.Ind2.stVal'', //tcs1s | tcs1s=?,
31 | Comal | Pemalang 1 | D29 | TCS 1 FAIL PHS T | BCU_TCS_1_FAIL_PHS.T | tcs1t | D29CTRL/GGIO26.Ind4.stVal | Boolean | ADD `tcs1t` CHAR(10) NOT NULL AFTER `tcs1s`, | ''D29CTRL/GGIO26.Ind4.stVal'', //tcs1t | tcs1t=?,
32 | Comal | Pemalang 1 | D29 | TCS 2 FAIL PHS R | BCU_TCS_2_FAIL_PHS.R | tcs2r | D29CTRL/GGIO26.Ind1.stVal | Boolean | ADD `tcs2r` CHAR(10) NOT NULL AFTER `tcs1t`, | ''D29CTRL/GGIO26.Ind1.stVal'', //tcs2r | tcs2r=?,
33 | Comal | Pemalang 1 | D29 | TCS 2 FAIL PHS S | BCU_TCS_2_FAIL_PHS.S | tcs2s | D29CTRL/GGIO26.Ind3.stVal | Boolean | ADD `tcs2s` CHAR(10) NOT NULL AFTER `tcs2r`, | ''D29CTRL/GGIO26.Ind3.stVal'', //tcs2s | tcs2s=?,
34 | Comal | Pemalang 1 | D29 | TCS 2 FAIL PHS T | BCU_TCS_2_FAIL_PHS.T | tcs2t | D29CTRL/GGIO26.Ind5.stVal | Boolean | ADD `tcs2t` CHAR(10) NOT NULL AFTER `tcs2s`, | ''D29CTRL/GGIO26.Ind5.stVal'', //tcs2t | tcs2t=?,
35 | Comal | Pemalang 1 | D29 | MOTOR MCB TRIP | BCU_MOTOR_MCB_TRIP | motormcb | D29CTRL/GGIO26.Ind7.stVal | Boolean | ADD `motormcb` CHAR(10) NOT NULL AFTER `tcs2t`, | ''D29CTRL/GGIO26.Ind7.stVal'', //motormcb | motormcb=?,
36 | Comal | Pemalang 1 | D29 | LINE VT MBC TRIP | BCU_LINE_VT_MCB_TRIP | vtmcb | D29CTRL/GGIO26.Ind8.stVal | Boolean | ADD `vtmcb` CHAR(10) NOT NULL AFTER `motormcb`, | ''D29CTRL/GGIO26.Ind8.stVal'', //vtmcb | vtmcb=?,
37 | Comal | Pemalang 1 | D29 | PROTECTION SUPPLY FAIL | BCU_PROT_SUPPLY_FAIL | protsupply | D29CTRL/GGIO27.Ind1.stVal | Boolean | ADD `protsupply` CHAR(10) NOT NULL AFTER `vtmcb`, | ''D29CTRL/GGIO27.Ind1.stVal'', //protsupply | protsupply=?,
38 | Comal | Pemalang 1 | D29 | CONTROL SUPPLY FAIL | BCU_CTRL_SUPPLY_FAIL | ctrlsupply | D29CTRL/GGIO27.Ind2.stVal | Boolean | ADD `ctrlsupply` CHAR(10) NOT NULL AFTER `protsupply`, | ''D29CTRL/GGIO27.Ind2.stVal'', //ctrlsupply | ctrlsupply=?,
44 | Comal | Pemalang 1 | D29 | K861 OPERATE | BCU_LOCKOUT K861 | k861op | D29CTRL/GGIO17.Ind2.stVal | Boolean | ADD `k861op` CHAR(10) NOT NULL AFTER `ctrlsupply`, | ''D29CTRL/GGIO17.Ind2.stVal'', //k861op | k861op=?,
45 | Comal | Pemalang 1 | D29 | K862 OPERATE | BCU_LOCKOUT K862 | k862op | D29CTRL/GGIO17.Ind3.stVal | Boolean | ADD `k862op` CHAR(10) NOT NULL AFTER `k861op`, | ''D29CTRL/GGIO17.Ind3.stVal'', //k862op | k862op=?,
46 | Comal | Pemalang 1 | D29 | K863 OPERATE | BCU_LOCKOUT K863 | k863op | D29CTRL/GGIO17.Ind4.stVal | Boolean | ADD `k863op` CHAR(10) NOT NULL AFTER `k862op`, | ''D29CTRL/GGIO17.Ind4.stVal'', //k863op | k863op=?,
83 | Comal | Pemalang 1 | D29 | Q21 | VOLTAGE 150/PEMALANG 1 | statQ21 | D29CTRL/XSWI1.Pos.stVal |  | ADD `statQ21` CHAR(10) NOT NULL AFTER `k863op`, | ''D29CTRL/XSWI1.Pos.stVal'', //statQ21 | statQ21=?,
84 | Comal | Pemalang 1 | D29 | Q22 | VOLTAGE 150/PEMALANG 1 | statQ22 | D29CTRL/XSWI2.Pos.stVal |  | ADD `statQ22` CHAR(10) NOT NULL AFTER `statQ21`, | ''D29CTRL/XSWI2.Pos.stVal'', //statQ22 | statQ22=?,
85 | Comal | Pemalang 1 | D29 | Q50 | VOLTAGE 150/PEMALANG 1 | statQ50 | D29CTRL/XCBR1.Pos.stVal |  | ADD `statQ50` CHAR(10) NOT NULL AFTER `statQ22`, | ''D29CTRL/XCBR1.Pos.stVal'', //statQ50 | statQ50=?,
86 | Comal | Pemalang 1 | D29 | Q28 | VOLTAGE 150/PEMALANG 1 | statQ28 | D29CTRL/XSWI3.Pos.stVal |  | ADD `statQ28` CHAR(10) NOT NULL AFTER `statQ50`, | ''D29CTRL/XSWI3.Pos.stVal'', //statQ28 | statQ28=?,
87 | Comal | Pemalang 1 | D29 | Q38 | VOLTAGE 150/PEMALANG 1 | statQ38 | D29CTRL/XSWI4.Pos.stVal |  | ADD `statQ38` CHAR(10) NOT NULL AFTER `statQ28`, | ''D29CTRL/XSWI4.Pos.stVal'', //statQ38 | statQ38=?,
57 | Comal | Pemalang 1 | D28 | OCR OPERATED | F67_50/51P3.Op | ocrop | D28PROT/PTOC3.Op.general | Boolean | ADD `ocrop` CHAR(10) NOT NULL AFTER `statQ38`, | ''D28PROT/PTOC3.Op.general'', //ocrop | ocrop=?,
58 | Comal | Pemalang 1 | D28 | GFR OPERATED | SYTHETIC INFORMATION / PMLG2 GFR | gfrop1 | D28PROT/PTOC5.Op.general |  | ADD `gfrop1` CHAR(10) NOT NULL AFTER `ocrop`, | ''D28PROT/PTOC5.Op.general'', //gfrop1 | gfrop1=?,
59 | Comal | Pemalang 1 | D28 |  |  | gfrop2 | D28PROT/PTOC6.Op.general |  | ADD `gfrop2` CHAR(10) NOT NULL AFTER `gfrop1`, | ''D28PROT/PTOC6.Op.general'', //gfrop2 | gfrop2=?,
60 | Comal | Pemalang 1 | D28 |  |  | gfrop3 | D28PROT/PTOC7.Op.general |  | ADD `gfrop3` CHAR(10) NOT NULL AFTER `gfrop2`, | ''D28PROT/PTOC7.Op.general'', //gfrop3 | gfrop3=?,
61 | Comal | Pemalang 1 | D28 |  |  | gfrop4 | D28PROT/PTOC8.Op.general |  | ADD `gfrop4` CHAR(10) NOT NULL AFTER `gfrop3`, | ''D28PROT/PTOC8.Op.general'', //gfrop4 | gfrop4=?,
63 | Comal | Pemalang 1 | D28 |  |  | r1 | D28PROT/PTRC1.Op.phsA |  | ADD `r1` CHAR(10) NOT NULL AFTER `gfrop4`, | ''D28PROT/PTRC1.Op.phsA'', //r1 | r1=?,
64 | Comal | Pemalang 1 | D28 |  |  | r2 | D28PROT/PTOC3.Op.phsA |  | ADD `r2` CHAR(10) NOT NULL AFTER `r1`, | ''D28PROT/PTOC3.Op.phsA'', //r2 | r2=?,
65 | Comal | Pemalang 1 | D28 |  |  | r3 | D28PROT/PTOC5.Op.phsA |  | ADD `r3` CHAR(10) NOT NULL AFTER `r2`, | ''D28PROT/PTOC5.Op.phsA'', //r3 | r3=?,
66 | Comal | Pemalang 1 | D28 |  |  | r4 | D28PROT/PTOC6.Op.phsA |  | ADD `r4` CHAR(10) NOT NULL AFTER `r3`, | ''D28PROT/PTOC6.Op.phsA'', //r4 | r4=?,
67 | Comal | Pemalang 1 | D28 |  |  | r5 | D28PROT/PTOC7.Op.phsA |  | ADD `r5` CHAR(10) NOT NULL AFTER `r4`, | ''D28PROT/PTOC7.Op.phsA'', //r5 | r5=?,
68 | Comal | Pemalang 1 | D28 |  |  | r6 | D28PROT/PTOC8.Op.phsA |  | ADD `r6` CHAR(10) NOT NULL AFTER `r5`, | ''D28PROT/PTOC8.Op.phsA'', //r6 | r6=?,
70 | Comal | Pemalang 1 | D28 |  |  | s1 | D28PROT/PTRC1.Op.phsB |  | ADD `s1` CHAR(10) NOT NULL AFTER `r6`, | ''D28PROT/PTRC1.Op.phsB'', //s1 | s1=?,
71 | Comal | Pemalang 1 | D28 |  |  | s2 | D28PROT/PTOC3.Op.phsB |  | ADD `s2` CHAR(10) NOT NULL AFTER `s1`, | ''D28PROT/PTOC3.Op.phsB'', //s2 | s2=?,
72 | Comal | Pemalang 1 | D28 |  |  | s3 | D28PROT/PTOC5.Op.phsB |  | ADD `s3` CHAR(10) NOT NULL AFTER `s2`, | ''D28PROT/PTOC5.Op.phsB'', //s3 | s3=?,
73 | Comal | Pemalang 1 | D28 |  |  | s4 | D28PROT/PTOC6.Op.phsB |  | ADD `s4` CHAR(10) NOT NULL AFTER `s3`, | ''D28PROT/PTOC6.Op.phsB'', //s4 | s4=?,
74 | Comal | Pemalang 1 | D28 |  |  | s5 | D28PROT/PTOC7.Op.phsB |  | ADD `s5` CHAR(10) NOT NULL AFTER `s4`, | ''D28PROT/PTOC7.Op.phsB'', //s5 | s5=?,
75 | Comal | Pemalang 1 | D28 |  |  | s6 | D28PROT/PTOC8.Op.phsB |  | ADD `s6` CHAR(10) NOT NULL AFTER `s5`, | ''D28PROT/PTOC8.Op.phsB'', //s6 | s6=?,
77 | Comal | Pemalang 1 | D28 |  |  | t1 | D28PROT/PTRC1.Op.phsC |  | ADD `t1` CHAR(10) NOT NULL AFTER `s6`, | ''D28PROT/PTRC1.Op.phsC'', //t1 | t1=?,
78 | Comal | Pemalang 1 | D28 |  |  | t2 | D28PROT/PTOC3.Op.phsC |  | ADD `t2` CHAR(10) NOT NULL AFTER `t1`, | ''D28PROT/PTOC3.Op.phsC'', //t2 | t2=?,
79 | Comal | Pemalang 1 | D28 |  |  | t3 | D28PROT/PTOC5.Op.phsC |  | ADD `t3` CHAR(10) NOT NULL AFTER `t2`, | ''D28PROT/PTOC5.Op.phsC'', //t3 | t3=?,
80 | Comal | Pemalang 1 | D28 |  |  | t4 | D28PROT/PTOC6.Op.phsC |  | ADD `t4` CHAR(10) NOT NULL AFTER `t3`, | ''D28PROT/PTOC6.Op.phsC'', //t4 | t4=?,
81 | Comal | Pemalang 1 | D28 |  |  | t5 | D28PROT/PTOC7.Op.phsC |  | ADD `t5` CHAR(10) NOT NULL AFTER `t4`, | ''D28PROT/PTOC7.Op.phsC'', //t5 | t5=?,
82 | Comal | Pemalang 1 | D28 |  |  | t6 | D28PROT/PTOC8.Op.phsC |  | ADD `t6` CHAR(10) NOT NULL AFTER `t5`, | ''D28PROT/PTOC8.Op.phsC'', //t6 | t6=?,
12 | Comal | Pemalang 1 | D27 | AR LOCKOUT | F87L_CB1.79.AR_Blkd | arlockout | D27PROT/GGIO39.Alm7.stVal | Boolean | ADD `arlockout` CHAR(10) NOT NULL AFTER `t6`, | ''D27PROT/GGIO39.Alm7.stVal'', //arlockout | arlockout=?,
39 | Comal | Pemalang 1 | D27 | CB UNHEALTHY | F87L_BI_CB_UNHEALTHY | cbunhealthy | LD0D27/GGIO3.Ind5.stVal | Boolean | ADD `cbunhealthy` CHAR(10) NOT NULL AFTER `arlockout`, | ''LD0D27/GGIO3.Ind5.stVal'', //cbunhealthy | cbunhealthy=?,
40 | Comal | Pemalang 1 | D27 | AIDED SEND | F87L_FO1.Send1 | aidedsend | D27PROT/PSCH2.TxSigPhA.stVal | Boolean | ADD `aidedsend` CHAR(10) NOT NULL AFTER `cbunhealthy`, | ''D27PROT/PSCH2.TxSigPhA.stVal'', //aidedsend | aidedsend=?,
41 | Comal | Pemalang 1 | D27 | DEF SEND | F87L_FO1.Send4 | defsend | D27PROT/PSCH1.ProTx.stVal | Boolean | ADD `defsend` CHAR(10) NOT NULL AFTER `aidedsend`, | ''D27PROT/PSCH1.ProTx.stVal'', //defsend | defsend=?,
42 | Comal | Pemalang 1 | D27 | AIDED RECEIVE | F87L_85-1.Recv1 | aidedreceive | D27PROT/PSCH2.RxSigPhA.stVal | Boolean | ADD `aidedreceive` CHAR(10) NOT NULL AFTER `defsend`, | ''D27PROT/PSCH2.RxSigPhA.stVal'', //aidedreceive | aidedreceive=?,
43 | Comal | Pemalang 1 | D27 | DEF RECEIVE | F87L_85-1.Recv2 | defreceive | D27PROT/PSCH1.ProRx.stVal | Boolean | ADD `defreceive` CHAR(10) NOT NULL AFTER `aidedreceive`, | ''D27PROT/PSCH1.ProRx.stVal'', //defreceive | defreceive=?,
47 | Comal | Pemalang 1 | D27 | DIFFERENTIAL OPERATED | F87L_87L.Op | diffop | D27PROT/PDIF2.Op.general | Boolean | ADD `diffop` CHAR(10) NOT NULL AFTER `defreceive`, | ''D27PROT/PDIF2.Op.general'', //diffop | diffop=?,
48 | Comal | Pemalang 1 | D27 | DISTANCE ZONE 1 OPERATED | F87L_21Q1.Op | z1op | D27PROT/PDIS4.Op.general | Boolean | ADD `z1op` CHAR(10) NOT NULL AFTER `diffop`, | ''D27PROT/PDIS4.Op.general'', //z1op | z1op=?,
49 | Comal | Pemalang 1 | D27 | DISTANCE ZONE 2 OPERATED | F87L_21Q2.Op | z2op | D27PROT/PDIS7.Op.general | Boolean | ADD `z2op` CHAR(10) NOT NULL AFTER `z1op`, | ''D27PROT/PDIS7.Op.general'', //z2op | z2op=?,
50 | Comal | Pemalang 1 | D27 | DISTANCE ZONE 3 OPERATED | F87L_21Q3.Op | z3op | D27PROT/PDIS8.Op.general | Boolean | ADD `z3op` CHAR(10) NOT NULL AFTER `z2op`, | ''D27PROT/PDIS8.Op.general'', //z3op | z3op=?,
51 | Comal | Pemalang 1 | D27 | SOTF OPERATED | F87L_21SOTF.Op | sotfop | D27PROT/GGIO18.ACTSO7.general | Boolean | ADD `sotfop` CHAR(10) NOT NULL AFTER `z3op`, | ''D27PROT/GGIO18.ACTSO7.general'', //sotfop | sotfop=?,
52 | Comal | Pemalang 1 | D27 | AUTO RECLOSE | F87L_CB1.79.Close | autoreclose | D27PROT/RREC1.Op.general |  | ADD `autoreclose` CHAR(10) NOT NULL AFTER `sotfop`, | ''D27PROT/RREC1.Op.general'', //autoreclose | autoreclose=?,
53 | Comal | Pemalang 1 | D27 | AIDED OPERATED | F87L_85.Op_Z | aidedop | D27PROT/PSCH2.Op.general | Boolean | ADD `aidedop` CHAR(10) NOT NULL AFTER `autoreclose`, | ''D27PROT/PSCH2.Op.general'', //aidedop | aidedop=?,
54 | Comal | Pemalang 1 | D27 | DEF OPERATED | F87L_85.Op_DEF | defop | D27PROT/PTOC27.Op.general | Boolean | ADD `defop` CHAR(10) NOT NULL AFTER `aidedop`, | ''D27PROT/PTOC27.Op.general'', //defop | defop=?,
55 | Comal | Pemalang 1 | D27 | POWER SWING BLOCK | F87L_78.St | psb | D27PROT/RPSB2.Str.general | Boolean | ADD `psb` CHAR(10) NOT NULL AFTER `defop`, | ''D27PROT/RPSB2.Str.general'', //psb | psb=?,
56 | Comal | Pemalang 1 | D27 | FO F87L ALARM | F87L_FO1.Alm | fof87lalarm | D27PROT/GGIO25.Alm7.stVal |  | ADD `fof87lalarm` CHAR(10) NOT NULL AFTER `psb`, | ''D27PROT/GGIO25.Alm7.stVal'', //fof87lalarm | fof87lalarm=?,
62 | Comal | Pemalang 1 | D27 | PMLNG 1 PH R | SYTHETIC INFORMATION / PMLG2 PH R | r_diff | D27PROT/GGIO39.Alm1.stVal |  | ADD `r_diff` CHAR(10) NOT NULL AFTER `fof87lalarm`, | ''D27PROT/GGIO39.Alm1.stVal'', //r_diff | r_diff=?,
69 | Comal | Pemalang 1 | D27 | PMLNG 1 PH S | SYTHETIC INFORMATION / PMLG2 PH S | s_diff | D27PROT/GGIO39.Alm2.stVal |  | ADD `s_diff` CHAR(10) NOT NULL AFTER `r_diff`, | ''D27PROT/GGIO39.Alm2.stVal'', //s_diff | s_diff=?,
76 | Comal | Pemalang 1 | D27 | PMLNG 1 PH T | SYTHETIC INFORMATION / PMLG2 PH T | t_diff | D27PROT/GGIO39.Alm3.stVal |  | ADD `t_diff` CHAR(10) NOT NULL AFTER `s_diff`, | ''D27PROT/GGIO39.Alm3.stVal'', //t_diff | t_diff=?,
5 | Comal | Pemalang 1 | D34 | BCU FAIL | BCU_PMLG1_BCU_FAIL | bcufail | D34CTRL/GGIO19.Ind8.stVal | Boolean | ADD `bcufail` CHAR(10) NOT NULL AFTER `t_diff`, | ''D34CTRL/GGIO19.Ind8.stVal'', //bcufail | bcufail=?,
6 | Comal | Pemalang 1 | D34 | ETHERNET FAIL | BCU_PMLG1_U11_FAIL | etherfail | D34CTRL/GGIO20.Ind1.stVal | Boolean | ADD `etherfail` CHAR(10) NOT NULL AFTER `bcufail`, | ''D34CTRL/GGIO20.Ind1.stVal'', //etherfail | etherfail=?,
9 | Comal | Pemalang 1 | D34 | BUSCOUPLER CLOSE | BCU_CB_Q0.2_CLOSED | buscouplerclose | D34CTRL/GGIO23.Ind8.stVal | Boolean | ADD `buscouplerclose` CHAR(10) NOT NULL AFTER `etherfail`, | ''D34CTRL/GGIO23.Ind8.stVal'', //buscouplerclose | buscouplerclose=?,
23 | Comal | Pemalang 1 | D36 | OLS OPERATED | BCU_OLS_PEMALANG-1 | olsop | D36CTRL/GGIO29.Ind4.stVal | Boolean | ADD `olsop` CHAR(10) NOT NULL AFTER `buscouplerclose`, | ''D36CTRL/GGIO29.Ind4.stVal'', //olsop | olsop=?,

## PEMALANG 2
No | Gardu Induk | Bay | IED | HMI | POINT | DATABASE |  | Type |  | " | String Objectt | QUERY SQL
1 | Comal | Pemalang 2 | D32 | F87L FAIL | BCU_F87l_FAIL | f87lfail | D32CTRL/GGIO17.Ind8.stVal | Boolean |  | ADD `f87lfail` CHAR(10) NOT NULL AFTER `bay`, | ''D32CTRL/GGIO17.Ind8.stVal'', //f87lfail | f87lfail=?,
2 | Comal | Pemalang 2 | D32 | F87L ALARM | BCU_F87l_ALARM | f87lalarm | D32CTRL/GGIO18.Ind1.stVal | Boolean |  | ADD `f87lalarm` CHAR(10) NOT NULL AFTER `f87lfail`, | ''D32CTRL/GGIO18.Ind1.stVal'', //f87lalarm | f87lalarm=?,
3 | Comal | Pemalang 2 | D32 | F50 FAIL | BCU_F50_FAIL | f50fail | D32CTRL/GGIO18.Ind4.stVal | Boolean |  | ADD `f50fail` CHAR(10) NOT NULL AFTER `f87lalarm`, | ''D32CTRL/GGIO18.Ind4.stVal'', //f50fail | f50fail=?,
4 | Comal | Pemalang 2 | D32 | F50 ALARM | BCU_F50_ALARM | f50alarm | D32CTRL/GGIO18.Ind5.stVal | Boolean |  | ADD `f50alarm` CHAR(10) NOT NULL AFTER `f50fail`, | ''D32CTRL/GGIO18.Ind5.stVal'', //f50alarm | f50alarm=?,
5 | Comal | Pemalang 2 | D34 | BCU FAIL | BCU_PMLG2_BCU_FAIL | bcufail | D34CTRL/GGIO20.Ind5.stVal | Boolean |  | ADD `bcufail` CHAR(10) NOT NULL AFTER `f50alarm`, | ''D34CTRL/GGIO20.Ind5.stVal'', //bcufail | bcufail=?,
6 | Comal | Pemalang 2 | D34 | ETHERNET FAIL | BCU_PMLG2_U11_FAIL | etherfail | D34CTRL/GGIO20.Ind6.stVal | Boolean |  | ADD `etherfail` CHAR(10) NOT NULL AFTER `bcufail`, | ''D34CTRL/GGIO20.Ind6.stVal'', //etherfail | etherfail=?,
7 | Comal | Pemalang 2 | D32 | MCB AC | BCU_MCB_AC | mcbac | D32CTRL/GGIO17.Ind7.stVal | Boolean |  | ADD `mcbac` CHAR(10) NOT NULL AFTER `etherfail`, | ''D32CTRL/GGIO17.Ind7.stVal'', //mcbac | mcbac=?,
8 | Comal | Pemalang 2 | D32 | AUX DC SUPPLY | BCU_MCB_AUX_DC_SUPPLY | auxdcsupply | D32CTRL/GGIO19.Ind4.stVal | Boolean |  | ADD `auxdcsupply` CHAR(10) NOT NULL AFTER `mcbac`, | ''D32CTRL/GGIO19.Ind4.stVal'', //auxdcsupply | auxdcsupply=?,
9 | Comal | Pemalang 2 | D34 | BUSCOUPLER CLOSE | BCU_CB_Q0.2_CLOSED | buscouplerclose | D34CTRL/GGIO23.Ind8.stVal | Boolean |  | ADD `buscouplerclose` CHAR(10) NOT NULL AFTER `auxdcsupply`, | ''D34CTRL/GGIO23.Ind8.stVal'', //buscouplerclose | buscouplerclose=?,
10 | Comal | Pemalang 2 | D32 | Q21 AND Q22 CLOSE | BCU_Q21_AND_Q22_CLOSE | q21q22close | D32CTRL/GGIO19.Ind7.stVal | Boolean |  | ADD `q21q22close` CHAR(10) NOT NULL AFTER `buscouplerclose`, | ''D32CTRL/GGIO19.Ind7.stVal'', //q21q22close | q21q22close=?,
11 | Comal | Pemalang 2 | D32 | CB SRING CHARGE FAIL | BCU_CB_SPRING_CHRG_FAIL | cbsringchargefail | D32CTRL/GGIO20.Ind6.stVal | Boolean |  | ADD `cbsringchargefail` CHAR(10) NOT NULL AFTER `q21q22close`, | ''D32CTRL/GGIO20.Ind6.stVal'', //cbsringchargefail | cbsringchargefail=?,
12 | Comal | Pemalang 2 | D30 | AR LOCKOUT | F87L_CB1.79.AR_Blkd | arlockout | D30PROT/GGIO39.Alm7.stVal | Boolean |  | ADD `arlockout` CHAR(10) NOT NULL AFTER `cbsringchargefail`, | ''D30PROT/GGIO39.Alm7.stVal'', //arlockout | arlockout=?,
13 | Comal | Pemalang 2 | D32 | CB MOTOR MCB TRIP | BCU_CB_MOTOR_MCB_TRIP | cbmotormcbtrip | D32CTRL/GGIO20.Ind7.stVal | Boolean |  | ADD `cbmotormcbtrip` CHAR(10) NOT NULL AFTER `arlockout`, | ''D32CTRL/GGIO20.Ind7.stVal'', //cbmotormcbtrip | cbmotormcbtrip=?,
14 | Comal | Pemalang 2 | D32 | CB PHS R CLOSE SPRING UNCHARGE | BCU_CB_PHS.R_CLS_SPRING_UNCHRG | springfailR | D32CTRL/GGIO20.Ind8.stVal | Boolean |  | ADD `springfailR` CHAR(10) NOT NULL AFTER `cbmotormcbtrip`, | ''D32CTRL/GGIO20.Ind8.stVal'', //springfailR | springfailR=?,
15 | Comal | Pemalang 2 | D32 | CB PHS S CLOSE SPRING UNCHARGE | BCU_CB_PHS.S_CLS_SPRING_UNCHRG | springfailS | D32CTRL/GGIO21.Ind1.stVal | Boolean |  | ADD `springfailS` CHAR(10) NOT NULL AFTER `springfailR`, | ''D32CTRL/GGIO21.Ind1.stVal'', //springfailS | springfailS=?,
16 | Comal | Pemalang 2 | D32 | CB PHS T CLOSE SPRING UNCHARGE | BCU_CB_PHS.T_CLS_SPRING_UNCHRG | springfailT | D32CTRL/GGIO21.Ind2.stVal | Boolean |  | ADD `springfailT` CHAR(10) NOT NULL AFTER `springfailS`, | ''D32CTRL/GGIO21.Ind2.stVal'', //springfailT | springfailT=?,
17 | Comal | Pemalang 2 | D32 | SF6 STAGE 2 BLOCK | BCU_SF6 STAGE 2 BLOK | sf6block | D32CTRL/GGIO21.Ind3.stVal | Boolean |  | ADD `sf6block` CHAR(10) NOT NULL AFTER `springfailT`, | ''D32CTRL/GGIO21.Ind3.stVal'', //sf6block | sf6block=?,
18 | Comal | Pemalang 2 | D32 | TRIP CIRCUIT 2 BLOCKED | BCU_TRIP_CIRCUIT_2_BLOCKED | tcs2block | D32CTRL/GGIO21.Ind4.stVal | Boolean |  | ADD `tcs2block` CHAR(10) NOT NULL AFTER `sf6block`, | ''D32CTRL/GGIO21.Ind4.stVal'', //tcs2block | tcs2block=?,
19 | Comal | Pemalang 2 | D32 | SF6 STAGE 1 ALARM | BCU_SF6 STAGE 1 ALARM | sf6alarm | D32CTRL/GGIO21.Ind5.stVal | Boolean |  | ADD `sf6alarm` CHAR(10) NOT NULL AFTER `tcs2block`, | ''D32CTRL/GGIO21.Ind5.stVal'', //sf6alarm | sf6alarm=?,
20 | Comal | Pemalang 2 | D32 | CB ALARM AC CIRCUIT | BCU_CB_ALARM_AC_CIRCUIT | cbalarmac | D32CTRL/GGIO22.Ind1.stVal | Boolean |  | ADD `cbalarmac` CHAR(10) NOT NULL AFTER `sf6alarm`, | ''D32CTRL/GGIO22.Ind1.stVal'', //cbalarmac | cbalarmac=?,
21 | Comal | Pemalang 2 | D32 | CB POLE DISCREPANCY | BCU_CB POLE DISCREPANCY | poledis | D32CTRL/GGIO22.Ind3.stVal | Boolean |  | ADD `poledis` CHAR(10) NOT NULL AFTER `cbalarmac`, | ''D32CTRL/GGIO22.Ind3.stVal'', //poledis | poledis=?,
22 | Comal | Pemalang 2 | D32 | DS Q21 MOTOR MCB TRIP | BCU_DS_Q21_MOTOR_MCB_TRIP | q21motor | D32CTRL/GGIO22.Ind8.stVal | Boolean |  | ADD `q21motor` CHAR(10) NOT NULL AFTER `poledis`, | ''D32CTRL/GGIO22.Ind8.stVal'', //q21motor | q21motor=?,
23 | Comal | Pemalang 2 | D36 | OLS OPERATED | BCU_OLS_PEMALANG-2 | olsop | D36CTRL/GGIO29.Ind5.stVal | Boolean |  | ADD `olsop` CHAR(10) NOT NULL AFTER `q21motor`, | ''D36CTRL/GGIO29.Ind5.stVal'', //olsop | olsop=?,
24 | Comal | Pemalang 2 | D32 | DS Q21 CONTROL MCB TRIP | BCU_DS_Q21_CONTROL_MCB_TRIP | q21control | D32CTRL/GGIO23.Ind1.stVal | Boolean |  | ADD `q21control` CHAR(10) NOT NULL AFTER `olsop`, | ''D32CTRL/GGIO23.Ind1.stVal'', //q21control | q21control=?,
25 | Comal | Pemalang 2 | D32 | DS Q22 MOTOR MCB TRIP | BCU_DS_Q22_MOTOR_MCB_TRIP | q22motor | D32CTRL/GGIO23.Ind7.stVal | Boolean |  | ADD `q22motor` CHAR(10) NOT NULL AFTER `q21control`, | ''D32CTRL/GGIO23.Ind7.stVal'', //q22motor | q22motor=?,
26 | Comal | Pemalang 2 | D32 | DS Q22 CONTROL MCB TRIP | BCU_DS_Q22_CONTROL_MCB_TRIP | q22control | D32CTRL/GGIO23.Ind8.stVal | Boolean |  | ADD `q22control` CHAR(10) NOT NULL AFTER `q22motor`, | ''D32CTRL/GGIO23.Ind8.stVal'', //q22control | q22control=?,
27 | Comal | Pemalang 2 | D32 | DS Q28 MOTOR MCB TRIP | BCU_DS_Q28_MOTOR_MCB_TRIP | q28motor | D32CTRL/GGIO25.Ind1.stVal | Boolean |  | ADD `q28motor` CHAR(10) NOT NULL AFTER `q22control`, | ''D32CTRL/GGIO25.Ind1.stVal'', //q28motor | q28motor=?,
28 | Comal | Pemalang 2 | D32 | DS Q28 CONTROL MCB TRIP | BCU_DS_Q28_CONTROL_MCB_TRIP | q28control | D32CTRL/GGIO25.Ind2.stVal | Boolean |  | ADD `q28control` CHAR(10) NOT NULL AFTER `q28motor`, | ''D32CTRL/GGIO25.Ind2.stVal'', //q28control | q28control=?,
29 | Comal | Pemalang 2 | D32 | TCS 1 FAIL PHS R | BCU_TCS_1_FAIL_PHS.R | tcs1r | D32CTRL/GGIO25.Ind8.stVal | Boolean |  | ADD `tcs1r` CHAR(10) NOT NULL AFTER `q28control`, | ''D32CTRL/GGIO25.Ind8.stVal'', //tcs1r | tcs1r=?,
30 | Comal | Pemalang 2 | D32 | TCS 1 FAIL PHS S | BCU_TCS_1_FAIL_PHS.S | tcs1s | D32CTRL/GGIO26.Ind2.stVal | Boolean |  | ADD `tcs1s` CHAR(10) NOT NULL AFTER `tcs1r`, | ''D32CTRL/GGIO26.Ind2.stVal'', //tcs1s | tcs1s=?,
31 | Comal | Pemalang 2 | D32 | TCS 1 FAIL PHS T | BCU_TCS_1_FAIL_PHS.T | tcs1t | D32CTRL/GGIO26.Ind4.stVal | Boolean |  | ADD `tcs1t` CHAR(10) NOT NULL AFTER `tcs1s`, | ''D32CTRL/GGIO26.Ind4.stVal'', //tcs1t | tcs1t=?,
32 | Comal | Pemalang 2 | D32 | TCS 2 FAIL PHS R | BCU_TCS_2_FAIL_PHS.R | tcs2r | D32CTRL/GGIO26.Ind1.stVal | Boolean |  | ADD `tcs2r` CHAR(10) NOT NULL AFTER `tcs1t`, | ''D32CTRL/GGIO26.Ind1.stVal'', //tcs2r | tcs2r=?,
33 | Comal | Pemalang 2 | D32 | TCS 2 FAIL PHS S | BCU_TCS_2_FAIL_PHS.S | tcs2s | D32CTRL/GGIO26.Ind3.stVal | Boolean |  | ADD `tcs2s` CHAR(10) NOT NULL AFTER `tcs2r`, | ''D32CTRL/GGIO26.Ind3.stVal'', //tcs2s | tcs2s=?,
34 | Comal | Pemalang 2 | D32 | TCS 2 FAIL PHS T | BCU_TCS_2_FAIL_PHS.T | tcs2t | D32CTRL/GGIO26.Ind5.stVal | Boolean |  | ADD `tcs2t` CHAR(10) NOT NULL AFTER `tcs2s`, | ''D32CTRL/GGIO26.Ind5.stVal'', //tcs2t | tcs2t=?,
35 | Comal | Pemalang 2 | D32 | MOTOR MCB TRIP | BCU_MOTOR_MCB_TRIP | motormcb | D32CTRL/GGIO26.Ind7.stVal | Boolean |  | ADD `motormcb` CHAR(10) NOT NULL AFTER `tcs2t`, | ''D32CTRL/GGIO26.Ind7.stVal'', //motormcb | motormcb=?,
36 | Comal | Pemalang 2 | D32 | LINE VT MBC TRIP | BCU_LINE_VT_MCB_TRIP | vtmcb | D32CTRL/GGIO26.Ind8.stVal | Boolean |  | ADD `vtmcb` CHAR(10) NOT NULL AFTER `motormcb`, | ''D32CTRL/GGIO26.Ind8.stVal'', //vtmcb | vtmcb=?,
37 | Comal | Pemalang 2 | D32 | PROTECTION SUPPLY FAIL | BCU_PROT_SUPPLY_FAIL | protsupply | D32CTRL/GGIO27.Ind1.stVal | Boolean |  | ADD `protsupply` CHAR(10) NOT NULL AFTER `vtmcb`, | ''D32CTRL/GGIO27.Ind1.stVal'', //protsupply | protsupply=?,
38 | Comal | Pemalang 2 | D32 | CONTROL SUPPLY FAIL | BCU_CTRL_SUPPLY_FAIL | ctrlsupply | D32CTRL/GGIO27.Ind2.stVal | Boolean |  | ADD `ctrlsupply` CHAR(10) NOT NULL AFTER `protsupply`, | ''D32CTRL/GGIO27.Ind2.stVal'', //ctrlsupply | ctrlsupply=?,
39 | Comal | Pemalang 2 | D30 | CB UNHEALTHY | F87L_BI_CB_UNHEALTHY | cbunhealthy | LD0D30/GGIO3.Ind5.stVal | Boolean |  | ADD `cbunhealthy` CHAR(10) NOT NULL AFTER `ctrlsupply`, | ''LD0D30/GGIO3.Ind5.stVal'', //cbunhealthy | cbunhealthy=?,
40 | Comal | Pemalang 2 | D30 | AIDED SEND | F87L_FO1.Send1 | aidedsend | D30PROT/PSCH2.TxSigPhA.stVal | Boolean |  | ADD `aidedsend` CHAR(10) NOT NULL AFTER `cbunhealthy`, | ''D30PROT/PSCH2.TxSigPhA.stVal'', //aidedsend | aidedsend=?,
41 | Comal | Pemalang 2 | D30 | DEF SEND | F87L_FO1.Send4 | defsend | D30PROT/PSCH1.ProTx.stVal | Boolean |  | ADD `defsend` CHAR(10) NOT NULL AFTER `aidedsend`, | ''D30PROT/PSCH1.ProTx.stVal'', //defsend | defsend=?,
42 | Comal | Pemalang 2 | D30 | AIDED RECEIVE | F87L_85-1.Recv1 | aidedreceive | D30PROT/PSCH2.RxSigPhA.stVal | Boolean |  | ADD `aidedreceive` CHAR(10) NOT NULL AFTER `defsend`, | ''D30PROT/PSCH2.RxSigPhA.stVal'', //aidedreceive | aidedreceive=?,
43 | Comal | Pemalang 2 | D30 | DEF RECEIVE | F87L_85-1.Recv2 | defreceive | D30PROT/PSCH1.ProRx.stVal | Boolean |  | ADD `defreceive` CHAR(10) NOT NULL AFTER `aidedreceive`, | ''D30PROT/PSCH1.ProRx.stVal'', //defreceive | defreceive=?,
44 | Comal | Pemalang 2 | D32 | K861 OPERATE | BCU_LOCKOUT K861 | k861op | D32CTRL/GGIO17.Ind2.stVal | Boolean |  | ADD `k861op` CHAR(10) NOT NULL AFTER `defreceive`, | ''D32CTRL/GGIO17.Ind2.stVal'', //k861op | k861op=?,
45 | Comal | Pemalang 2 | D32 | K862 OPERATE | BCU_LOCKOUT K862 | k862op | D32CTRL/GGIO17.Ind3.stVal | Boolean |  | ADD `k862op` CHAR(10) NOT NULL AFTER `k861op`, | ''D32CTRL/GGIO17.Ind3.stVal'', //k862op | k862op=?,
46 | Comal | Pemalang 2 | D32 | K863 OPERATE | BCU_LOCKOUT K863 | k863op | D32CTRL/GGIO17.Ind4.stVal | Boolean |  | ADD `k863op` CHAR(10) NOT NULL AFTER `k862op`, | ''D32CTRL/GGIO17.Ind4.stVal'', //k863op | k863op=?,
47 | Comal | Pemalang 2 | D30 | DIFFERENTIAL OPERATED | F87L_87L.Op | diffop | D30PROT/PDIF2.Op.general | Boolean |  | ADD `diffop` CHAR(10) NOT NULL AFTER `k863op`, | ''D30PROT/PDIF2.Op.general'', //diffop | diffop=?,
48 | Comal | Pemalang 2 | D30 | DISTANCE ZONE 1 OPERATED | F87L_21Q1.Op | z1op | D30PROT/PDIS4.Op.general | Boolean |  | ADD `z1op` CHAR(10) NOT NULL AFTER `diffop`, | ''D30PROT/PDIS4.Op.general'', //z1op | z1op=?,
49 | Comal | Pemalang 2 | D30 | DISTANCE ZONE 2 OPERATED | F87L_21Q2.Op | z2op | D30PROT/PDIS7.Op.general | Boolean |  | ADD `z2op` CHAR(10) NOT NULL AFTER `z1op`, | ''D30PROT/PDIS7.Op.general'', //z2op | z2op=?,
50 | Comal | Pemalang 2 | D30 | DISTANCE ZONE 3 OPERATED | F87L_21Q3.Op | z3op | D30PROT/PDIS8.Op.general | Boolean |  | ADD `z3op` CHAR(10) NOT NULL AFTER `z2op`, | ''D30PROT/PDIS8.Op.general'', //z3op | z3op=?,
51 | Comal | Pemalang 2 | D30 | SOTF OPERATED | F87L_21SOTF.Op | sotfop | D30PROT/GGIO19.ACTSO7.general | Boolean |  | ADD `sotfop` CHAR(10) NOT NULL AFTER `z3op`, | ''D30PROT/GGIO19.ACTSO7.general'', //sotfop | sotfop=?,
52 | Comal | Pemalang 2 | D30 | AUTO RECLOSE | F87L_CB1.79.Close | autoreclose | D30PROT/RREC1.Op.general |  |  | ADD `autoreclose` CHAR(10) NOT NULL AFTER `sotfop`, | ''D30PROT/RREC1.Op.general'', //autoreclose | autoreclose=?,
53 | Comal | Pemalang 2 | D30 | AIDED OPERATED | F87L_85.Op_Z | aidedop | D30PROT/PSCH2.Op.general | Boolean |  | ADD `aidedop` CHAR(10) NOT NULL AFTER `autoreclose`, | ''D30PROT/PSCH2.Op.general'', //aidedop | aidedop=?,
54 | Comal | Pemalang 2 | D30 | DEF OPERATED | F87L_85.Op_DEF | defop | D30PROT/PTOC27.Op.general | Boolean |  | ADD `defop` CHAR(10) NOT NULL AFTER `aidedop`, | ''D30PROT/PTOC27.Op.general'', //defop | defop=?,
55 | Comal | Pemalang 2 | D30 | POWER SWING BLOCK | F87L_78.St | psb | D30PROT/RPSB2.Str.general | Boolean |  | ADD `psb` CHAR(10) NOT NULL AFTER `defop`, | ''D30PROT/RPSB2.Str.general'', //psb | psb=?,
56 | Comal | Pemalang 2 | D30 | FO F87L ALARM | F87L_FO1.Alm | fof87lalarm | D30PROT/GGIO25.Alm7.stVal |  |  | ADD `fof87lalarm` CHAR(10) NOT NULL AFTER `psb`, | ''D30PROT/GGIO25.Alm7.stVal'', //fof87lalarm | fof87lalarm=?,
57 | Comal | Pemalang 2 | D31 | OCR OPERATED | F67_50/51P3.Op | ocrop | D31PROT/PTOC3.Op.general | Boolean |  | ADD `ocrop` CHAR(10) NOT NULL AFTER `fof87lalarm`, | ''D31PROT/PTOC3.Op.general'', //ocrop | ocrop=?,
58 | Comal | Pemalang 2 | D31 | GFR OPERATED | SYTHETIC INFORMATION / PMLG2 GFR | gfrop1 | D31PROT/PTOC5.Op.general |  |  | ADD `gfrop1` CHAR(10) NOT NULL AFTER `ocrop`, | ''D31PROT/PTOC5.Op.general'', //gfrop1 | gfrop1=?,
59 | Comal | Pemalang 2 | D31 |  |  | gfrop2 | D31PROT/PTOC6.Op.general |  |  | ADD `gfrop2` CHAR(10) NOT NULL AFTER `gfrop1`, | ''D31PROT/PTOC6.Op.general'', //gfrop2 | gfrop2=?,
60 | Comal | Pemalang 2 | D31 |  |  | gfrop3 | D31PROT/PTOC7.Op.general |  |  | ADD `gfrop3` CHAR(10) NOT NULL AFTER `gfrop2`, | ''D31PROT/PTOC7.Op.general'', //gfrop3 | gfrop3=?,
61 | Comal | Pemalang 2 | D31 |  |  | gfrop4 | D31PROT/PTOC8.Op.general |  |  | ADD `gfrop4` CHAR(10) NOT NULL AFTER `gfrop3`, | ''D31PROT/PTOC8.Op.general'', //gfrop4 | gfrop4=?,
62 | Comal | Pemalang 2 | D30 | PMLNG 2 PH R | SYTHETIC INFORMATION / PMLG2 PH R | r_diff | D30PROT/GGIO39.Alm1.stVal |  |  | ADD `r_diff` CHAR(10) NOT NULL AFTER `gfrop4`, | ''D30PROT/GGIO39.Alm1.stVal'', //r_diff | r_diff=?,
63 | Comal | Pemalang 2 | D31 |  |  | r1 | D31PROT/PTRC1.Op.phsA |  |  | ADD `r1` CHAR(10) NOT NULL AFTER `r_diff`, | ''D31PROT/PTRC1.Op.phsA'', //r1 | r1=?,
64 | Comal | Pemalang 2 | D31 |  |  | r2 | D31PROT/PTOC3.Op.phsA |  |  | ADD `r2` CHAR(10) NOT NULL AFTER `r1`, | ''D31PROT/PTOC3.Op.phsA'', //r2 | r2=?,
65 | Comal | Pemalang 2 | D31 |  |  | r3 | D31PROT/PTOC5.Op.phsA |  |  | ADD `r3` CHAR(10) NOT NULL AFTER `r2`, | ''D31PROT/PTOC5.Op.phsA'', //r3 | r3=?,
66 | Comal | Pemalang 2 | D31 |  |  | r4 | D31PROT/PTOC6.Op.phsA |  |  | ADD `r4` CHAR(10) NOT NULL AFTER `r3`, | ''D31PROT/PTOC6.Op.phsA'', //r4 | r4=?,
67 | Comal | Pemalang 2 | D31 |  |  | r5 | D31PROT/PTOC7.Op.phsA |  |  | ADD `r5` CHAR(10) NOT NULL AFTER `r4`, | ''D31PROT/PTOC7.Op.phsA'', //r5 | r5=?,
68 | Comal | Pemalang 2 | D31 |  |  | r6 | D31PROT/PTOC8.Op.phsA |  |  | ADD `r6` CHAR(10) NOT NULL AFTER `r5`, | ''D31PROT/PTOC8.Op.phsA'', //r6 | r6=?,
69 | Comal | Pemalang 2 | D30 | PMLNG 2 PH S | SYTHETIC INFORMATION / PMLG2 PH S | s_diff | D30PROT/GGIO39.Alm2.stVal |  |  | ADD `s_diff` CHAR(10) NOT NULL AFTER `r6`, | ''D30PROT/GGIO39.Alm2.stVal'', //s_diff | s_diff=?,
70 | Comal | Pemalang 2 | D31 |  |  | s1 | D31PROT/PTRC1.Op.phsB |  |  | ADD `s1` CHAR(10) NOT NULL AFTER `s_diff`, | ''D31PROT/PTRC1.Op.phsB'', //s1 | s1=?,
71 | Comal | Pemalang 2 | D31 |  |  | s2 | D31PROT/PTOC3.Op.phsB |  |  | ADD `s2` CHAR(10) NOT NULL AFTER `s1`, | ''D31PROT/PTOC3.Op.phsB'', //s2 | s2=?,
72 | Comal | Pemalang 2 | D31 |  |  | s3 | D31PROT/PTOC5.Op.phsB |  |  | ADD `s3` CHAR(10) NOT NULL AFTER `s2`, | ''D31PROT/PTOC5.Op.phsB'', //s3 | s3=?,
73 | Comal | Pemalang 2 | D31 |  |  | s4 | D31PROT/PTOC6.Op.phsB |  |  | ADD `s4` CHAR(10) NOT NULL AFTER `s3`, | ''D31PROT/PTOC6.Op.phsB'', //s4 | s4=?,
74 | Comal | Pemalang 2 | D31 |  |  | s5 | D31PROT/PTOC7.Op.phsB |  |  | ADD `s5` CHAR(10) NOT NULL AFTER `s4`, | ''D31PROT/PTOC7.Op.phsB'', //s5 | s5=?,
75 | Comal | Pemalang 2 | D31 |  |  | s6 | D31PROT/PTOC8.Op.phsB |  |  | ADD `s6` CHAR(10) NOT NULL AFTER `s5`, | ''D31PROT/PTOC8.Op.phsB'', //s6 | s6=?,
76 | Comal | Pemalang 2 | D30 | PMLNG 2 PH T | SYTHETIC INFORMATION / PMLG2 PH T | t_diff | D30PROT/GGIO39.Alm3.stVal |  |  | ADD `t_diff` CHAR(10) NOT NULL AFTER `s6`, | ''D30PROT/GGIO39.Alm3.stVal'', //t_diff | t_diff=?,
77 | Comal | Pemalang 2 | D31 |  |  | t1 | D31PROT/PTRC1.Op.phsC |  |  | ADD `t1` CHAR(10) NOT NULL AFTER `t_diff`, | ''D31PROT/PTRC1.Op.phsC'', //t1 | t1=?,
78 | Comal | Pemalang 2 | D31 |  |  | t2 | D31PROT/PTOC3.Op.phsC |  |  | ADD `t2` CHAR(10) NOT NULL AFTER `t1`, | ''D31PROT/PTOC3.Op.phsC'', //t2 | t2=?,
79 | Comal | Pemalang 2 | D31 |  |  | t3 | D31PROT/PTOC5.Op.phsC |  |  | ADD `t3` CHAR(10) NOT NULL AFTER `t2`, | ''D31PROT/PTOC5.Op.phsC'', //t3 | t3=?,
80 | Comal | Pemalang 2 | D31 |  |  | t4 | D31PROT/PTOC6.Op.phsC |  |  | ADD `t4` CHAR(10) NOT NULL AFTER `t3`, | ''D31PROT/PTOC6.Op.phsC'', //t4 | t4=?,
81 | Comal | Pemalang 2 | D31 |  |  | t5 | D31PROT/PTOC7.Op.phsC |  |  | ADD `t5` CHAR(10) NOT NULL AFTER `t4`, | ''D31PROT/PTOC7.Op.phsC'', //t5 | t5=?,
82 | Comal | Pemalang 2 | D31 |  |  | t6 | D31PROT/PTOC8.Op.phsC |  |  | ADD `t6` CHAR(10) NOT NULL AFTER `t5`, | ''D31PROT/PTOC8.Op.phsC'', //t6 | t6=?,
83 | Comal | Pemalang 2 | D32 | Q21 | VOLTAGE 150/PEMALANG 2 | statQ21 | D32CTRL/XSWI1.Pos.stVal |  |  | ADD `statQ21` CHAR(10) NOT NULL AFTER `t6`, | ''D32CTRL/XSWI1.Pos.stVal'', //statQ21 | statQ21=?,
84 | Comal | Pemalang 2 | D32 | Q22 | VOLTAGE 150/PEMALANG 2 | statQ22 | D32CTRL/XSWI2.Pos.stVal |  |  | ADD `statQ22` CHAR(10) NOT NULL AFTER `statQ21`, | ''D32CTRL/XSWI2.Pos.stVal'', //statQ22 | statQ22=?,
85 | Comal | Pemalang 2 | D32 | Q50 | VOLTAGE 150/PEMALANG 2 | statQ50 | D32CTRL/XCBR1.Pos.stVal |  |  | ADD `statQ50` CHAR(10) NOT NULL AFTER `statQ22`, | ''D32CTRL/XCBR1.Pos.stVal'', //statQ50 | statQ50=?,
86 | Comal | Pemalang 2 | D32 | Q28 | VOLTAGE 150/PEMALANG 2 | statQ28 | D32CTRL/XSWI3.Pos.stVal |  |  | ADD `statQ28` CHAR(10) NOT NULL AFTER `statQ50`, | ''D32CTRL/XSWI3.Pos.stVal'', //statQ28 | statQ28=?,
87 | Comal | Pemalang 2 | D32 | Q38 | VOLTAGE 150/PEMALANG 2 | statQ38 | D32CTRL/XSWI4.Pos.stVal |  |  | ADD `statQ38` CHAR(10) NOT NULL AFTER `statQ28`, | ''D32CTRL/XSWI4.Pos.stVal'', //statQ38 | statQ38=?,
|  |  |  | BUS1 |  |  | D34CTRL/CILO11.EnaCls.stVal | ON=TRUE | BISA SALAH
|  |  |  | BUS2 |  |  | D34CTRL/CILO12.EnaCls.stVal | ON=FALSE | BISA SALAH
41
23
19
83

## PEKALONGAN 2
No | Gardu Induk | Bay | IED | HMI | POINT | DATABASE |  | Type
1 | Comal | Pekalongan 2 | D26 | F87L FAIL | BCU_F87l_FAIL | f87lfail | D26CTRL/GGIO17.Ind8.stVal | Boolean | ADD `f87lalarm` CHAR(10) NOT NULL AFTER `bay`,
2 | Comal | Pekalongan 2 | D26 | F87L ALARM | BCU_F87l_ALARM | f87lalarm | D26CTRL/GGIO18.Ind1.stVal | Boolean | ADD `f50fail` CHAR(10) NOT NULL AFTER `f87lalarm`,
3 | Comal | Pekalongan 2 | D26 | F50 FAIL | BCU_F50_FAIL | f50fail | D26CTRL/GGIO18.Ind4.stVal | Boolean | ADD `f50alarm` CHAR(10) NOT NULL AFTER `f50fail`,
4 | Comal | Pekalongan 2 | D26 | F50 ALARM | BCU_F50_ALARM | f50alarm | D26CTRL/GGIO18.Ind5.stVal | Boolean | ADD `bcufail` CHAR(10) NOT NULL AFTER `f50alarm`,
5 | Comal | Pekalongan 2 | D34 | BCU FAIL | BCU_PKLG2_BCU_FAIL | bcufail | D34CTRL/GGIO19.Ind6.stVal | Boolean | ADD `etherfail` CHAR(10) NOT NULL AFTER `bcufail`,
6 | Comal | Pekalongan 2 | D34 | ETHERNET FAIL | BCU_PKLG2_U11_FAIL | etherfail | D34CTRL/GGIO19.Ind7.stVal | Boolean | ADD `mcbac` CHAR(10) NOT NULL AFTER `etherfail`,
7 | Comal | Pekalongan 2 | D26 | MCB AC | BCU_MCB_AC | mcbac | D26CTRL/GGIO17.Ind7.stVal | Boolean | ADD `auxdcsupply` CHAR(10) NOT NULL AFTER `mcbac`,
8 | Comal | Pekalongan 2 | D26 | AUX DC SUPPLY | BCU_MCB_AUX_DC_SUPPLY | auxdcsupply | D26CTRL/GGIO19.Ind4.stVal | Boolean | ADD `buscouplerclose` CHAR(10) NOT NULL AFTER `auxdcsupply`,
9 | Comal | Pekalongan 2 | D34 | BUSCOUPLER CLOSE | BCU_CB_Q0.2_CLOSED | buscouplerclose | D34CTRL/GGIO23.Ind8.stVal | Boolean | ADD `q21q22close` CHAR(10) NOT NULL AFTER `buscouplerclose`,
10 | Comal | Pekalongan 2 | D26 | Q21 AND Q22 CLOSE | BCU_Q21_AND_Q22_CLOSE | q21q22close | D26CTRL/GGIO19.Ind7.stVal | Boolean | ADD `cbsringchargefail` CHAR(10) NOT NULL AFTER `q21q22close`,
11 | Comal | Pekalongan 2 | D26 | CB SRING CHARGE FAIL | BCU_CB_SPRING_CHRG_FAIL | cbsringchargefail | D26CTRL/GGIO20.Ind6.stVal | Boolean | ADD `arlockout` CHAR(10) NOT NULL AFTER `cbsringchargefail`,
12 | Comal | Pekalongan 2 | D24 | AR LOCKOUT | F87L_CB1.79.AR_Blkd | arlockout | D24PROT/GGIO39.Alm7.stVal | Boolean | ADD `cbmotormcbtrip` CHAR(10) NOT NULL AFTER `arlockout`,
13 | Comal | Pekalongan 2 | D26 | CB MOTOR MCB TRIP | BCU_CB_MOTOR_MCB_TRIP | cbmotormcbtrip | D26CTRL/GGIO20.Ind7.stVal | Boolean | ADD `springfailR` CHAR(10) NOT NULL AFTER `cbmotormcbtrip`,
14 | Comal | Pekalongan 2 | D26 | CB PHS R CLOSE SPRING UNCHARGE | BCU_CB_PHS.R_CLS_SPRING_UNCHRG | springfailR | D26CTRL/GGIO20.Ind8.stVal | Boolean | ADD `springfailS` CHAR(10) NOT NULL AFTER `springfailR`,
15 | Comal | Pekalongan 2 | D26 | CB PHS S CLOSE SPRING UNCHARGE | BCU_CB_PHS.S_CLS_SPRING_UNCHRG | springfailS | D26CTRL/GGIO21.Ind1.stVal | Boolean | ADD `springfailT` CHAR(10) NOT NULL AFTER `springfailS`,
16 | Comal | Pekalongan 2 | D26 | CB PHS T CLOSE SPRING UNCHARGE | BCU_CB_PHS.T_CLS_SPRING_UNCHRG | springfailT | D26CTRL/GGIO21.Ind2.stVal | Boolean | ADD `sf6block` CHAR(10) NOT NULL AFTER `springfailT`,
17 | Comal | Pekalongan 2 | D26 | SF6 STAGE 2 BLOCK | BCU_SF6 STAGE 2 BLOK | sf6block | D26CTRL/GGIO21.Ind3.stVal | Boolean | ADD `tcs2block` CHAR(10) NOT NULL AFTER `sf6block`,
18 | Comal | Pekalongan 2 | D26 | TRIP CIRCUIT 2 BLOCKED | BCU_TRIP_CIRCUIT_2_BLOCKED | tcs2block | D26CTRL/GGIO21.Ind4.stVal | Boolean | ADD `sf6alarm` CHAR(10) NOT NULL AFTER `tcs2block`,
19 | Comal | Pekalongan 2 | D26 | SF6 STAGE 1 ALARM | BCU_SF6 STAGE 1 ALARM | sf6alarm | D26CTRL/GGIO21.Ind5.stVal | Boolean | ADD `cbalarmac` CHAR(10) NOT NULL AFTER `sf6alarm`,
20 | Comal | Pekalongan 2 | D26 | CB ALARM AC CIRCUIT | BCU_CB_ALARM_AC_CIRCUIT | cbalarmac | D26CTRL/GGIO22.Ind1.stVal | Boolean | ADD `poledis` CHAR(10) NOT NULL AFTER `cbalarmac`,
21 | Comal | Pekalongan 2 | D26 | CB POLE DISCREPANCY | BCU_CB POLE DISCREPANCY | poledis | D26CTRL/GGIO22.Ind3.stVal | Boolean | ADD `q21motor` CHAR(10) NOT NULL AFTER `poledis`,
22 | Comal | Pekalongan 2 | D26 | DS Q21 MOTOR MCB TRIP | BCU_DS_Q21_MOTOR_MCB_TRIP | q21motor | D26CTRL/GGIO22.Ind8.stVal | Boolean | ADD `olsop` CHAR(10) NOT NULL AFTER `q21motor`,
23 | Comal | Pekalongan 2 | D36 | OLS OPERATED | BCU_OLS_PEKALONGAN-2 | olsop | D36CTRL/GGIO29.Ind3.stVal | Boolean | ADD `q21control` CHAR(10) NOT NULL AFTER `olsop`,
24 | Comal | Pekalongan 2 | D26 | DS Q21 CONTROL MCB TRIP | BCU_DS_Q21_CONTROL_MCB_TRIP | q21control | D26CTRL/GGIO23.Ind1.stVal | Boolean | ADD `q22motor` CHAR(10) NOT NULL AFTER `q21control`,
25 | Comal | Pekalongan 2 | D26 | DS Q22 MOTOR MCB TRIP | BCU_DS_Q22_MOTOR_MCB_TRIP | q22motor | D26CTRL/GGIO23.Ind7.stVal | Boolean | ADD `q22control` CHAR(10) NOT NULL AFTER `q22motor`,
26 | Comal | Pekalongan 2 | D26 | DS Q22 CONTROL MCB TRIP | BCU_DS_Q22_CONTROL_MCB_TRIP | q22control | D26CTRL/GGIO23.Ind8.stVal | Boolean | ADD `q28motor` CHAR(10) NOT NULL AFTER `q22control`,
27 | Comal | Pekalongan 2 | D26 | DS Q28 MOTOR MCB TRIP | BCU_DS_Q28_MOTOR_MCB_TRIP | q28motor | D26CTRL/GGIO25.Ind1.stVal | Boolean | ADD `q28control` CHAR(10) NOT NULL AFTER `q28motor`,
28 | Comal | Pekalongan 2 | D26 | DS Q28 CONTROL MCB TRIP | BCU_DS_Q28_CONTROL_MCB_TRIP | q28control | D26CTRL/GGIO25.Ind2.stVal | Boolean | ADD `tcs1r` CHAR(10) NOT NULL AFTER `q28control`,
29 | Comal | Pekalongan 2 | D26 | TCS 1 FAIL PHS R | BCU_TCS_1_FAIL_PHS.R | tcs1r | D26CTRL/GGIO25.Ind8.stVal | Boolean | ADD `tcs1s` CHAR(10) NOT NULL AFTER `tcs1r`,
30 | Comal | Pekalongan 2 | D26 | TCS 1 FAIL PHS S | BCU_TCS_1_FAIL_PHS.S | tcs1s | D26CTRL/GGIO26.Ind2.stVal | Boolean | ADD `tcs1t` CHAR(10) NOT NULL AFTER `tcs1s`,
31 | Comal | Pekalongan 2 | D26 | TCS 1 FAIL PHS T | BCU_TCS_1_FAIL_PHS.T | tcs1t | D26CTRL/GGIO26.Ind4.stVal | Boolean | ADD `tcs2r` CHAR(10) NOT NULL AFTER `tcs1t`,
32 | Comal | Pekalongan 2 | D26 | TCS 2 FAIL PHS R | BCU_TCS_2_FAIL_PHS.R | tcs2r | D26CTRL/GGIO26.Ind1.stVal | Boolean | ADD `tcs2s` CHAR(10) NOT NULL AFTER `tcs2r`,
33 | Comal | Pekalongan 2 | D26 | TCS 2 FAIL PHS S | BCU_TCS_2_FAIL_PHS.S | tcs2s | D26CTRL/GGIO26.Ind3.stVal | Boolean | ADD `tcs2t` CHAR(10) NOT NULL AFTER `tcs2s`,
34 | Comal | Pekalongan 2 | D26 | TCS 2 FAIL PHS T | BCU_TCS_2_FAIL_PHS.T | tcs2t | D26CTRL/GGIO26.Ind5.stVal | Boolean | ADD `motormcb` CHAR(10) NOT NULL AFTER `tcs2t`,
35 | Comal | Pekalongan 2 | D26 | MOTOR MCB TRIP | BCU_MOTOR_MCB_TRIP | motormcb | D26CTRL/GGIO26.Ind7.stVal | Boolean | ADD `vtmcb` CHAR(10) NOT NULL AFTER `motormcb`,
36 | Comal | Pekalongan 2 | D26 | LINE VT MBC TRIP | BCU_LINE_VT_MCB_TRIP | vtmcb | D26CTRL/GGIO26.Ind8.stVal | Boolean | ADD `protsupply` CHAR(10) NOT NULL AFTER `vtmcb`,
37 | Comal | Pekalongan 2 | D26 | PROTECTION SUPPLY FAIL | BCU_PROT_SUPPLY_FAIL | protsupply | D26CTRL/GGIO27.Ind1.stVal | Boolean | ADD `ctrlsupply` CHAR(10) NOT NULL AFTER `protsupply`,
38 | Comal | Pekalongan 2 | D26 | CONTROL SUPPLY FAIL | BCU_CTRL_SUPPLY_FAIL | ctrlsupply | D26CTRL/GGIO27.Ind2.stVal | Boolean | ADD `cbunhealthy` CHAR(10) NOT NULL AFTER `ctrlsupply`,
39 | Comal | Pekalongan 2 | D24 | CB UNHEALTHY | F87L_BI_CB_UNHEALTHY | cbunhealthy | LD0D24/GGIO3.Ind5.stVal | Boolean | ADD `aidedsend` CHAR(10) NOT NULL AFTER `cbunhealthy`,
40 | Comal | Pekalongan 2 | D24 | AIDED SEND | F87L_FO1.Send1 | aidedsend | D24PROT/PSCH2.TxSigPhA.stVal | Boolean | ADD `defsend` CHAR(10) NOT NULL AFTER `aidedsend`,
41 | Comal | Pekalongan 2 | D24 | DEF SEND | F87L_FO1.Send4 | defsend | D24PROT/PSCH1.ProTx.stVal | Boolean | ADD `aidedreceive` CHAR(10) NOT NULL AFTER `defsend`,
42 | Comal | Pekalongan 2 | D24 | AIDED RECEIVE | F87L_85-1.Recv1 | aidedreceive | D24PROT/PSCH2.RxSigPhA.stVal | Boolean | ADD `defreceive` CHAR(10) NOT NULL AFTER `aidedreceive`,
43 | Comal | Pekalongan 2 | D24 | DEF RECEIVE | F87L_85-1.Recv2 | defreceive | D24PROT/PSCH1.ProRx.stVal | Boolean | ADD `k861op` CHAR(10) NOT NULL AFTER `defreceive`,
44 | Comal | Pekalongan 2 | D26 | K861 OPERATE | BCU_LOCKOUT K861 | k861op | D26CTRL/GGIO17.Ind2.stVal | Boolean | ADD `k862op` CHAR(10) NOT NULL AFTER `k861op`,
45 | Comal | Pekalongan 2 | D26 | K862 OPERATE | BCU_LOCKOUT K862 | k862op | D26CTRL/GGIO17.Ind3.stVal | Boolean | ADD `k863op` CHAR(10) NOT NULL AFTER `k862op`,
46 | Comal | Pekalongan 2 | D26 | K863 OPERATE | BCU_LOCKOUT K863 | k863op | D26CTRL/GGIO17.Ind4.stVal | Boolean | ADD `diffop` CHAR(10) NOT NULL AFTER `k863op`,
47 | Comal | Pekalongan 2 | D24 | DIFFERENTIAL OPERATED | F87L_87L.Op | diffop | D24PROT/PDIF2.Op.general | Boolean | ADD `z1op` CHAR(10) NOT NULL AFTER `diffop`,
48 | Comal | Pekalongan 2 | D24 | DISTANCE ZONE 1 OPERATED | F87L_21Q1.Op | z1op | D24PROT/PDIS4.Op.general | Boolean | ADD `z2op` CHAR(10) NOT NULL AFTER `z1op`,
49 | Comal | Pekalongan 2 | D24 | DISTANCE ZONE 2 OPERATED | F87L_21Q2.Op | z2op | D24PROT/PDIS7.Op.general | Boolean | ADD `z3op` CHAR(10) NOT NULL AFTER `z2op`,
50 | Comal | Pekalongan 2 | D24 | DISTANCE ZONE 3 OPERATED | F87L_21Q3.Op | z3op | D24PROT/PDIS8.Op.general | Boolean | ADD `sotfop` CHAR(10) NOT NULL AFTER `z3op`,
51 | Comal | Pekalongan 2 | D24 | SOTF OPERATED | F87L_21SOTF.Op | sotfop | D24PROT/GGIO18.ACTSO7.general | Boolean | ADD `autoreclose` CHAR(10) NOT NULL AFTER `sotfop`,
52 | Comal | Pekalongan 2 | D24 | AUTO RECLOSE | F87L_CB1.79.Close | autoreclose | D24PROT/RREC1.Op.general |  | ADD `aidedop` CHAR(10) NOT NULL AFTER `autoreclose`,
53 | Comal | Pekalongan 2 | D24 | AIDED OPERATED | F87L_85.Op_Z | aidedop | D24PROT/PSCH2.Op.general | Boolean | ADD `defop` CHAR(10) NOT NULL AFTER `aidedop`,
54 | Comal | Pekalongan 2 | D24 | DEF OPERATED | F87L_85.Op_DEF | defop | D24PROT/PTOC27.Op.general | Boolean | ADD `psb` CHAR(10) NOT NULL AFTER `defop`,
55 | Comal | Pekalongan 2 | D24 | POWER SWING BLOCK | F87L_78.St | psb | D24PROT/RPSB2.Str.general | Boolean | ADD `fof87lalarm` CHAR(10) NOT NULL AFTER `psb`,
56 | Comal | Pekalongan 2 | D24 | FO F87L ALARM | F87L_FO1.Alm | fof87lalarm | D24PROT/GGIO25.Alm7.stVal |  | ADD `ocrop` CHAR(10) NOT NULL AFTER `fof87lalarm`,
57 | Comal | Pekalongan 2 | D25 | OCR OPERATED | F67_50/51P3.Op | ocrop | D25PROT/PTOC3.Op.general | Boolean | ADD `gfrop1` CHAR(10) NOT NULL AFTER `ocrop`,
58 | Comal | Pekalongan 2 | D25 | GFR OPERATED | SYTHETIC INFORMATION / PMLG2 GFR | gfrop1 | D25PROT/PTOC5.Op.general |  | ADD `gfrop2` CHAR(10) NOT NULL AFTER `gfrop1`,
59 | Comal | Pekalongan 2 | D25 |  |  | gfrop2 | D25PROT/PTOC6.Op.general |  | ADD `gfrop3` CHAR(10) NOT NULL AFTER `gfrop2`,
60 | Comal | Pekalongan 2 | D25 |  |  | gfrop3 | D25PROT/PTOC7.Op.general |  | ADD `gfrop4` CHAR(10) NOT NULL AFTER `gfrop3`,
61 | Comal | Pekalongan 2 | D25 |  |  | gfrop4 | D25PROT/PTOC8.Op.general |  | ADD `r_diff` CHAR(10) NOT NULL AFTER `gfrop4`,
62 | Comal | Pekalongan 2 | D24 | PMLNG 1 PH R | SYTHETIC INFORMATION / PMLG2 PH R | r_diff | D24PROT/GGIO39.Alm1.stVal |  | ADD `r1` CHAR(10) NOT NULL AFTER `r_diff`,
63 | Comal | Pekalongan 2 | D25 |  |  | r1 | D25PROT/PTRC1.Op.phsA |  | ADD `r2` CHAR(10) NOT NULL AFTER `r1`,
64 | Comal | Pekalongan 2 | D25 |  |  | r2 | D25PROT/PTOC3.Op.phsA |  | ADD `r3` CHAR(10) NOT NULL AFTER `r2`,
65 | Comal | Pekalongan 2 | D25 |  |  | r3 | D25PROT/PTOC5.Op.phsA |  | ADD `r4` CHAR(10) NOT NULL AFTER `r3`,
66 | Comal | Pekalongan 2 | D25 |  |  | r4 | D25PROT/PTOC6.Op.phsA |  | ADD `r5` CHAR(10) NOT NULL AFTER `r4`,
67 | Comal | Pekalongan 2 | D25 |  |  | r5 | D25PROT/PTOC7.Op.phsA |  | ADD `r6` CHAR(10) NOT NULL AFTER `r5`,
68 | Comal | Pekalongan 2 | D25 |  |  | r6 | D25PROT/PTOC8.Op.phsA |  | ADD `s_diff` CHAR(10) NOT NULL AFTER `r6`,
69 | Comal | Pekalongan 2 | D24 | PMLNG 1 PH S | SYTHETIC INFORMATION / PMLG2 PH S | s_diff | D24PROT/GGIO39.Alm2.stVal |  | ADD `s1` CHAR(10) NOT NULL AFTER `s_diff`,
70 | Comal | Pekalongan 2 | D25 |  |  | s1 | D25PROT/PTRC1.Op.phsB |  | ADD `s2` CHAR(10) NOT NULL AFTER `s1`,
71 | Comal | Pekalongan 2 | D25 |  |  | s2 | D25PROT/PTOC3.Op.phsB |  | ADD `s3` CHAR(10) NOT NULL AFTER `s2`,
72 | Comal | Pekalongan 2 | D25 |  |  | s3 | D25PROT/PTOC5.Op.phsB |  | ADD `s4` CHAR(10) NOT NULL AFTER `s3`,
73 | Comal | Pekalongan 2 | D25 |  |  | s4 | D25PROT/PTOC6.Op.phsB |  | ADD `s5` CHAR(10) NOT NULL AFTER `s4`,
74 | Comal | Pekalongan 2 | D25 |  |  | s5 | D25PROT/PTOC7.Op.phsB |  | ADD `s6` CHAR(10) NOT NULL AFTER `s5`,
75 | Comal | Pekalongan 2 | D25 |  |  | s6 | D25PROT/PTOC8.Op.phsB |  | ADD `t_diff` CHAR(10) NOT NULL AFTER `s6`,
76 | Comal | Pekalongan 2 | D24 | PMLNG 1 PH T | SYTHETIC INFORMATION / PMLG2 PH T | t_diff | D24PROT/GGIO39.Alm3.stVal |  | ADD `t1` CHAR(10) NOT NULL AFTER `t_diff`,
77 | Comal | Pekalongan 2 | D25 |  |  | t1 | D25PROT/PTRC1.Op.phsC |  | ADD `t2` CHAR(10) NOT NULL AFTER `t1`,
78 | Comal | Pekalongan 2 | D25 |  |  | t2 | D25PROT/PTOC3.Op.phsC |  | ADD `t3` CHAR(10) NOT NULL AFTER `t2`,
79 | Comal | Pekalongan 2 | D25 |  |  | t3 | D25PROT/PTOC5.Op.phsC |  | ADD `t4` CHAR(10) NOT NULL AFTER `t3`,
80 | Comal | Pekalongan 2 | D25 |  |  | t4 | D25PROT/PTOC6.Op.phsC |  | ADD `t5` CHAR(10) NOT NULL AFTER `t4`,
81 | Comal | Pekalongan 2 | D25 |  |  | t5 | D25PROT/PTOC7.Op.phsC |  | ADD `t6` CHAR(10) NOT NULL AFTER `t5`,
82 | Comal | Pekalongan 2 | D25 |  |  | t6 | D25PROT/PTOC8.Op.phsC |  | ADD `statQ21` CHAR(10) NOT NULL AFTER `t6`,
83 | Comal | Pekalongan 2 | D26 | Q21 | VOLTAGE 150/PEKALONGAN 2 | statQ21 | D26CTRL/XSWI1.Pos.stVal |  | ADD `statQ22` CHAR(10) NOT NULL AFTER `statQ21`,
84 | Comal | Pekalongan 2 | D26 | Q22 | VOLTAGE 150/PEKALONGAN 2 | statQ22 | D26CTRL/XSWI2.Pos.stVal |  | ADD `statQ50` CHAR(10) NOT NULL AFTER `statQ22`,
85 | Comal | Pekalongan 2 | D26 | Q50 | VOLTAGE 150/PEKALONGAN 2 | statQ50 | D26CTRL/XCBR1.Pos.stVal |  | ADD `statQ28` CHAR(10) NOT NULL AFTER `statQ50`,
86 | Comal | Pekalongan 2 | D26 | Q28 | VOLTAGE 150/PEKALONGAN 2 | statQ28 | D26CTRL/XSWI3.Pos.stVal |  | ADD `statQ38` CHAR(10) NOT NULL AFTER `statQ28`,
87 | Comal | Pekalongan 2 | D26 | Q38 | VOLTAGE 150/PEKALONGAN 2 | statQ38 | D26CTRL/XSWI4.Pos.stVal |  | ADD `DATABASE` CHAR(10) NOT NULL AFTER `statQ38`,

## PEKALONGAN 1
No | Gardu Induk | Bay | IED | HMI | POINT | DATABASE |  | Type
1 | Comal | Pekalongan 1 | D23 | F87L FAIL | BCU_F87l_FAIL | f87lfail | D23CTRL/GGIO17.Ind8.stVal | Boolean | ADD `f87lalarm` CHAR(10) NOT NULL AFTER `bay`,
2 | Comal | Pekalongan 1 | D23 | F87L ALARM | BCU_F87l_ALARM | f87lalarm | D23CTRL/GGIO18.Ind1.stVal | Boolean | ADD `f50fail` CHAR(10) NOT NULL AFTER `f87lalarm`,
3 | Comal | Pekalongan 1 | D23 | F50 FAIL | BCU_F50_FAIL | f50fail | D23CTRL/GGIO18.Ind4.stVal | Boolean | ADD `f50alarm` CHAR(10) NOT NULL AFTER `f50fail`,
4 | Comal | Pekalongan 1 | D23 | F50 ALARM | BCU_F50_ALARM | f50alarm | D23CTRL/GGIO18.Ind5.stVal | Boolean | ADD `bcufail` CHAR(10) NOT NULL AFTER `f50alarm`,
5 | Comal | Pekalongan 1 | D34 | BCU FAIL | BCU_PKLG1_BCU_FAIL | bcufail | D34CTRL/GGIO19.Ind2.stVal | Boolean | ADD `etherfail` CHAR(10) NOT NULL AFTER `bcufail`,
6 | Comal | Pekalongan 1 | D34 | ETHERNET FAIL | BCU_PKLG1_U11_FAIL | etherfail | D34CTRL/GGIO19.Ind3.stVal | Boolean | ADD `mcbac` CHAR(10) NOT NULL AFTER `etherfail`,
7 | Comal | Pekalongan 1 | D23 | MCB AC | BCU_MCB_AC | mcbac | D23CTRL/GGIO17.Ind7.stVal | Boolean | ADD `auxdcsupply` CHAR(10) NOT NULL AFTER `mcbac`,
8 | Comal | Pekalongan 1 | D23 | AUX DC SUPPLY | BCU_MCB_AUX_DC_SUPPLY | auxdcsupply | D23CTRL/GGIO19.Ind4.stVal | Boolean | ADD `buscouplerclose` CHAR(10) NOT NULL AFTER `auxdcsupply`,
9 | Comal | Pekalongan 1 | D34 | BUSCOUPLER CLOSE | BCU_CB_Q0.2_CLOSED | buscouplerclose | D34CTRL/GGIO23.Ind8.stVal | Boolean | ADD `q21q22close` CHAR(10) NOT NULL AFTER `buscouplerclose`,
10 | Comal | Pekalongan 1 | D23 | Q21 AND Q22 CLOSE | BCU_Q21_AND_Q22_CLOSE | q21q22close | D23CTRL/GGIO19.Ind7.stVal | Boolean | ADD `cbsringchargefail` CHAR(10) NOT NULL AFTER `q21q22close`,
11 | Comal | Pekalongan 1 | D23 | CB SRING CHARGE FAIL | BCU_CB_SPRING_CHRG_FAIL | cbsringchargefail | D23CTRL/GGIO20.Ind6.stVal | Boolean | ADD `arlockout` CHAR(10) NOT NULL AFTER `cbsringchargefail`,
12 | Comal | Pekalongan 1 | D21 | AR LOCKOUT | F87L_CB1.79.AR_Blkd | arlockout | D21PROT/GGIO39.Alm7.stVal | Boolean | ADD `cbmotormcbtrip` CHAR(10) NOT NULL AFTER `arlockout`,
13 | Comal | Pekalongan 1 | D23 | CB MOTOR MCB TRIP | BCU_CB_MOTOR_MCB_TRIP | cbmotormcbtrip | D23CTRL/GGIO20.Ind7.stVal | Boolean | ADD `springfailR` CHAR(10) NOT NULL AFTER `cbmotormcbtrip`,
14 | Comal | Pekalongan 1 | D23 | CB PHS R CLOSE SPRING UNCHARGE | BCU_CB_PHS.R_CLS_SPRING_UNCHRG | springfailR | D23CTRL/GGIO20.Ind8.stVal | Boolean | ADD `springfailS` CHAR(10) NOT NULL AFTER `springfailR`,
15 | Comal | Pekalongan 1 | D23 | CB PHS S CLOSE SPRING UNCHARGE | BCU_CB_PHS.S_CLS_SPRING_UNCHRG | springfailS | D23CTRL/GGIO21.Ind1.stVal | Boolean | ADD `springfailT` CHAR(10) NOT NULL AFTER `springfailS`,
16 | Comal | Pekalongan 1 | D23 | CB PHS T CLOSE SPRING UNCHARGE | BCU_CB_PHS.T_CLS_SPRING_UNCHRG | springfailT | D23CTRL/GGIO21.Ind2.stVal | Boolean | ADD `sf6block` CHAR(10) NOT NULL AFTER `springfailT`,
17 | Comal | Pekalongan 1 | D23 | SF6 STAGE 2 BLOCK | BCU_SF6 STAGE 2 BLOK | sf6block | D23CTRL/GGIO21.Ind3.stVal | Boolean | ADD `tcs2block` CHAR(10) NOT NULL AFTER `sf6block`,
18 | Comal | Pekalongan 1 | D23 | TRIP CIRCUIT 2 BLOCKED | BCU_TRIP_CIRCUIT_2_BLOCKED | tcs2block | D23CTRL/GGIO21.Ind4.stVal | Boolean | ADD `sf6alarm` CHAR(10) NOT NULL AFTER `tcs2block`,
19 | Comal | Pekalongan 1 | D23 | SF6 STAGE 1 ALARM | BCU_SF6 STAGE 1 ALARM | sf6alarm | D23CTRL/GGIO21.Ind5.stVal | Boolean | ADD `cbalarmac` CHAR(10) NOT NULL AFTER `sf6alarm`,
20 | Comal | Pekalongan 1 | D23 | CB ALARM AC CIRCUIT | BCU_CB_ALARM_AC_CIRCUIT | cbalarmac | D23CTRL/GGIOD22.Ind1.stVal | Boolean | ADD `poledis` CHAR(10) NOT NULL AFTER `cbalarmac`,
21 | Comal | Pekalongan 1 | D23 | CB POLE DISCREPANCY | BCU_CB POLE DISCREPANCY | poledis | D23CTRL/GGIOD22.Ind3.stVal | Boolean | ADD `q21motor` CHAR(10) NOT NULL AFTER `poledis`,
22 | Comal | Pekalongan 1 | D23 | DS Q21 MOTOR MCB TRIP | BCU_DS_Q21_MOTOR_MCB_TRIP | q21motor | D23CTRL/GGIOD22.Ind8.stVal | Boolean | ADD `olsop` CHAR(10) NOT NULL AFTER `q21motor`,
23 | Comal | Pekalongan 1 | D36 | OLS OPERATED | BCU_OLS_PEKALONGAN-1 | olsop | D36CTRL/GGIO29.Ind2.stVal | Boolean | ADD `q21control` CHAR(10) NOT NULL AFTER `olsop`,
24 | Comal | Pekalongan 1 | D23 | DS Q21 CONTROL MCB TRIP | BCU_DS_Q21_CONTROL_MCB_TRIP | q21control | D23CTRL/GGIO23.Ind1.stVal | Boolean | ADD `q22motor` CHAR(10) NOT NULL AFTER `q21control`,
25 | Comal | Pekalongan 1 | D23 | DS Q22 MOTOR MCB TRIP | BCU_DS_Q22_MOTOR_MCB_TRIP | q22motor | D23CTRL/GGIO23.Ind7.stVal | Boolean | ADD `q22control` CHAR(10) NOT NULL AFTER `q22motor`,
26 | Comal | Pekalongan 1 | D23 | DS Q22 CONTROL MCB TRIP | BCU_DS_Q22_CONTROL_MCB_TRIP | q22control | D23CTRL/GGIO23.Ind8.stVal | Boolean | ADD `q28motor` CHAR(10) NOT NULL AFTER `q22control`,
27 | Comal | Pekalongan 1 | D23 | DS Q28 MOTOR MCB TRIP | BCU_DS_Q28_MOTOR_MCB_TRIP | q28motor | D23CTRL/GGIO25.Ind1.stVal | Boolean | ADD `q28control` CHAR(10) NOT NULL AFTER `q28motor`,
28 | Comal | Pekalongan 1 | D23 | DS Q28 CONTROL MCB TRIP | BCU_DS_Q28_CONTROL_MCB_TRIP | q28control | D23CTRL/GGIO25.Ind2.stVal | Boolean | ADD `tcs1r` CHAR(10) NOT NULL AFTER `q28control`,
29 | Comal | Pekalongan 1 | D23 | TCS 1 FAIL PHS R | BCU_TCS_1_FAIL_PHS.R | tcs1r | D23CTRL/GGIO26.Ind1.stVal | Boolean | ADD `tcs1s` CHAR(10) NOT NULL AFTER `tcs1r`,
30 | Comal | Pekalongan 1 | D23 | TCS 1 FAIL PHS S | BCU_TCS_1_FAIL_PHS.S | tcs1s | D23CTRL/GGIO26.Ind3.stVal | Boolean | ADD `tcs1t` CHAR(10) NOT NULL AFTER `tcs1s`,
31 | Comal | Pekalongan 1 | D23 | TCS 1 FAIL PHS T | BCU_TCS_1_FAIL_PHS.T | tcs1t | D23CTRL/GGIO26.Ind5.stVal | Boolean | ADD `tcs2r` CHAR(10) NOT NULL AFTER `tcs1t`,
32 | Comal | Pekalongan 1 | D23 | TCS 2 FAIL PHS R | BCU_TCS_2_FAIL_PHS.R | tcs2r | D23CTRL/GGIO26.Ind2.stVal | Boolean | ADD `tcs2s` CHAR(10) NOT NULL AFTER `tcs2r`,
33 | Comal | Pekalongan 1 | D23 | TCS 2 FAIL PHS S | BCU_TCS_2_FAIL_PHS.S | tcs2s | D23CTRL/GGIO26.Ind4.stVal | Boolean | ADD `tcs2t` CHAR(10) NOT NULL AFTER `tcs2s`,
34 | Comal | Pekalongan 1 | D23 | TCS 2 FAIL PHS T | BCU_TCS_2_FAIL_PHS.T | tcs2t | D23CTRL/GGIO26.Ind6.stVal | Boolean | ADD `motormcb` CHAR(10) NOT NULL AFTER `tcs2t`,
35 | Comal | Pekalongan 1 | D23 | MOTOR MCB TRIP | BCU_MOTOR_MCB_TRIP | motormcb | D23CTRL/GGIO26.Ind7.stVal | Boolean | ADD `vtmcb` CHAR(10) NOT NULL AFTER `motormcb`,
36 | Comal | Pekalongan 1 | D23 | LINE VT MBC TRIP | BCU_LINE_VT_MCB_TRIP | vtmcb | D23CTRL/GGIO26.Ind8.stVal | Boolean | ADD `protsupply` CHAR(10) NOT NULL AFTER `vtmcb`,
37 | Comal | Pekalongan 1 | D23 | PROTECTION SUPPLY FAIL | BCU_PROT_SUPPLY_FAIL | protsupply | D23CTRL/GGIO27.Ind1.stVal | Boolean | ADD `ctrlsupply` CHAR(10) NOT NULL AFTER `protsupply`,
38 | Comal | Pekalongan 1 | D23 | CONTROL SUPPLY FAIL | BCU_CTRL_SUPPLY_FAIL | ctrlsupply | D23CTRL/GGIO27.Ind2.stVal | Boolean | ADD `cbunhealthy` CHAR(10) NOT NULL AFTER `ctrlsupply`,
39 | Comal | Pekalongan 1 | D21 | CB UNHEALTHY | F87L_BI_CB_UNHEALTHY | cbunhealthy | LD0D21/GGIO3.Ind5.stVal | Boolean | ADD `aidedsend` CHAR(10) NOT NULL AFTER `cbunhealthy`,
40 | Comal | Pekalongan 1 | D21 | AIDED SEND | F87L_FO1.Send1 | aidedsend | D21PROT/PSCH2.TxSigPhA.stVal | Boolean | ADD `defsend` CHAR(10) NOT NULL AFTER `aidedsend`,
41 | Comal | Pekalongan 1 | D21 | DEF SEND | F87L_FO1.Send4 | defsend | D21PROT/PSCH1.ProTx.stVal | Boolean | ADD `aidedreceive` CHAR(10) NOT NULL AFTER `defsend`,
42 | Comal | Pekalongan 1 | D21 | AIDED RECEIVE | F87L_85-1.Recv1 | aidedreceive | D21PROT/PSCH2.RxSigPhA.stVal | Boolean | ADD `defreceive` CHAR(10) NOT NULL AFTER `aidedreceive`,
43 | Comal | Pekalongan 1 | D21 | DEF RECEIVE | F87L_85-1.Recv2 | defreceive | D21PROT/PSCH1.ProRx.stVal | Boolean | ADD `k861op` CHAR(10) NOT NULL AFTER `defreceive`,
44 | Comal | Pekalongan 1 | D23 | K861 OPERATE | BCU_LOCKOUT K861 | k861op | D23CTRL/GGIO17.Ind2.stVal | Boolean | ADD `k862op` CHAR(10) NOT NULL AFTER `k861op`,
45 | Comal | Pekalongan 1 | D23 | K862 OPERATE | BCU_LOCKOUT K862 | k862op | D23CTRL/GGIO17.Ind3.stVal | Boolean | ADD `k863op` CHAR(10) NOT NULL AFTER `k862op`,
46 | Comal | Pekalongan 1 | D23 | K863 OPERATE | BCU_LOCKOUT K863 | k863op | D23CTRL/GGIO17.Ind4.stVal | Boolean | ADD `diffop` CHAR(10) NOT NULL AFTER `k863op`,
47 | Comal | Pekalongan 1 | D21 | DIFFERENTIAL OPERATED | F87L_87L.Op | diffop | D21PROT/PDIF2.Op.general | Boolean | ADD `z1op` CHAR(10) NOT NULL AFTER `diffop`,
48 | Comal | Pekalongan 1 | D21 | DISTANCE ZONE 1 OPERATED | F87L_21Q1.Op | z1op | D21PROT/PDIS4.Op.general | Boolean | ADD `z2op` CHAR(10) NOT NULL AFTER `z1op`,
49 | Comal | Pekalongan 1 | D21 | DISTANCE ZONE 2 OPERATED | F87L_21Q2.Op | z2op | D21PROT/PDIS7.Op.general | Boolean | ADD `z3op` CHAR(10) NOT NULL AFTER `z2op`,
50 | Comal | Pekalongan 1 | D21 | DISTANCE ZONE 3 OPERATED | F87L_21Q3.Op | z3op | D21PROT/PDIS8.Op.general | Boolean | ADD `sotfop` CHAR(10) NOT NULL AFTER `z3op`,
51 | Comal | Pekalongan 1 | D21 | SOTF OPERATED | F87L_21SOTF.Op | sotfop | D21PROT/GGIO18.ACTSO7.general | Boolean | ADD `autoreclose` CHAR(10) NOT NULL AFTER `sotfop`,
52 | Comal | Pekalongan 1 | D21 | AUTO RECLOSE | F87L_CB1.79.Close | autoreclose | D21PROT/RREC1.Op.general |  | ADD `aidedop` CHAR(10) NOT NULL AFTER `autoreclose`,
53 | Comal | Pekalongan 1 | D21 | AIDED OPERATED | F87L_85.Op_Z | aidedop | D21PROT/PSCH2.Op.general | Boolean | ADD `defop` CHAR(10) NOT NULL AFTER `aidedop`,
54 | Comal | Pekalongan 1 | D21 | DEF OPERATED | F87L_85.Op_DEF | defop | D21PROT/PTOC27.Op.general | Boolean | ADD `psb` CHAR(10) NOT NULL AFTER `defop`,
55 | Comal | Pekalongan 1 | D21 | POWER SWING BLOCK | F87L_78.St | psb | D21PROT/RPSB2.Str.general | Boolean | ADD `fof87lalarm` CHAR(10) NOT NULL AFTER `psb`,
56 | Comal | Pekalongan 1 | D21 | FO F87L ALARM | F87L_FO1.Alm | fof87lalarm | D21PROT/GGIO25.Alm7.stVal |  | ADD `ocrop` CHAR(10) NOT NULL AFTER `fof87lalarm`,
57 | Comal | Pekalongan 1 | D22 | OCR OPERATED | F67_50/51P3.Op | ocrop | D22PROT/PTOC3.Op.general | Boolean | ADD `gfrop1` CHAR(10) NOT NULL AFTER `ocrop`,
58 | Comal | Pekalongan 1 | D22 | GFR OPERATED | SYTHETIC INFORMATION / PMLG2 GFR | gfrop1 | D22PROT/PTOC5.Op.general |  | ADD `gfrop2` CHAR(10) NOT NULL AFTER `gfrop1`,
59 | Comal | Pekalongan 1 | D22 |  |  | gfrop2 | D22PROT/PTOC6.Op.general |  | ADD `gfrop3` CHAR(10) NOT NULL AFTER `gfrop2`,
60 | Comal | Pekalongan 1 | D22 |  |  | gfrop3 | D22PROT/PTOC7.Op.general |  | ADD `gfrop4` CHAR(10) NOT NULL AFTER `gfrop3`,
61 | Comal | Pekalongan 1 | D22 |  |  | gfrop4 | D22PROT/PTOC8.Op.general |  | ADD `gfrop4` CHAR(10) NOT NULL AFTER `gfrop4`,
62 | Comal | Pekalongan 1 | D21 | PMLNG 1 PH R | SYTHETIC INFORMATION / PMLG2 PH R | gfrop4 | D21PROT/GGIO39.Alm1.stVal |  | ADD `r1` CHAR(10) NOT NULL AFTER `gfrop4`,
63 | Comal | Pekalongan 1 | D22 |  |  | r1 | D22PROT/PTRC1.Op.phsA |  | ADD `r2` CHAR(10) NOT NULL AFTER `r1`,
64 | Comal | Pekalongan 1 | D22 |  |  | r2 | D22PROT/PTOC3.Op.phsA |  | ADD `r3` CHAR(10) NOT NULL AFTER `r2`,
65 | Comal | Pekalongan 1 | D22 |  |  | r3 | D22PROT/PTOC5.Op.phsA |  | ADD `r4` CHAR(10) NOT NULL AFTER `r3`,
66 | Comal | Pekalongan 1 | D22 |  |  | r4 | D22PROT/PTOC6.Op.phsA |  | ADD `r5` CHAR(10) NOT NULL AFTER `r4`,
67 | Comal | Pekalongan 1 | D22 |  |  | r5 | D22PROT/PTOC7.Op.phsA |  | ADD `r6` CHAR(10) NOT NULL AFTER `r5`,
68 | Comal | Pekalongan 1 | D22 |  |  | r6 | D22PROT/PTOC8.Op.phsA |  | ADD `s_diff` CHAR(10) NOT NULL AFTER `r6`,
69 | Comal | Pekalongan 1 | D21 | PMLNG 1 PH S | SYTHETIC INFORMATION / PMLG2 PH S | s_diff | D21PROT/GGIO39.Alm2.stVal |  | ADD `s1` CHAR(10) NOT NULL AFTER `s_diff`,
70 | Comal | Pekalongan 1 | D22 |  |  | s1 | D22PROT/PTRC1.Op.phsB |  | ADD `s2` CHAR(10) NOT NULL AFTER `s1`,
71 | Comal | Pekalongan 1 | D22 |  |  | s2 | D22PROT/PTOC3.Op.phsB |  | ADD `s3` CHAR(10) NOT NULL AFTER `s2`,
72 | Comal | Pekalongan 1 | D22 |  |  | s3 | D22PROT/PTOC5.Op.phsB |  | ADD `s4` CHAR(10) NOT NULL AFTER `s3`,
73 | Comal | Pekalongan 1 | D22 |  |  | s4 | D22PROT/PTOC6.Op.phsB |  | ADD `s5` CHAR(10) NOT NULL AFTER `s4`,
74 | Comal | Pekalongan 1 | D22 |  |  | s5 | D22PROT/PTOC7.Op.phsB |  | ADD `s6` CHAR(10) NOT NULL AFTER `s5`,
75 | Comal | Pekalongan 1 | D22 |  |  | s6 | D22PROT/PTOC8.Op.phsB |  | ADD `t_diff` CHAR(10) NOT NULL AFTER `s6`,
76 | Comal | Pekalongan 1 | D21 | PMLNG 1 PH T | SYTHETIC INFORMATION / PMLG2 PH T | t_diff | D21PROT/GGIO39.Alm3.stVal |  | ADD `t1` CHAR(10) NOT NULL AFTER `t_diff`,
77 | Comal | Pekalongan 1 | D22 |  |  | t1 | D22PROT/PTRC1.Op.phsC |  | ADD `t2` CHAR(10) NOT NULL AFTER `t1`,
78 | Comal | Pekalongan 1 | D22 |  |  | t2 | D22PROT/PTOC3.Op.phsC |  | ADD `t3` CHAR(10) NOT NULL AFTER `t2`,
79 | Comal | Pekalongan 1 | D22 |  |  | t3 | D22PROT/PTOC5.Op.phsC |  | ADD `t4` CHAR(10) NOT NULL AFTER `t3`,
80 | Comal | Pekalongan 1 | D22 |  |  | t4 | D22PROT/PTOC6.Op.phsC |  | ADD `t5` CHAR(10) NOT NULL AFTER `t4`,
81 | Comal | Pekalongan 1 | D22 |  |  | t5 | D22PROT/PTOC7.Op.phsC |  | ADD `t6` CHAR(10) NOT NULL AFTER `t5`,
82 | Comal | Pekalongan 1 | D22 |  |  | t6 | D22PROT/PTOC8.Op.phsC |  | ADD `statQ21` CHAR(10) NOT NULL AFTER `t6`,
83 | Comal | Pekalongan 1 | D23 | Q21 | VOLTAGE 150/PEKALONGAN 1 | statQ21 | D23CTRL/XSWI1.Pos.stVal |  | ADD `statQ22` CHAR(10) NOT NULL AFTER `statQ21`,
84 | Comal | Pekalongan 1 | D23 | Q22 | VOLTAGE 150/PEKALONGAN 1 | statQ22 | D23CTRL/XSWI2.Pos.stVal |  | ADD `statQ50` CHAR(10) NOT NULL AFTER `statQ22`,
85 | Comal | Pekalongan 1 | D23 | Q50 | VOLTAGE 150/PEKALONGAN 1 | statQ50 | D23CTRL/XCBR1.Pos.stVal |  | ADD `statQ28` CHAR(10) NOT NULL AFTER `statQ50`,
86 | Comal | Pekalongan 1 | D23 | Q28 | VOLTAGE 150/PEKALONGAN 1 | statQ28 | D23CTRL/XSWI3.Pos.stVal |  | ADD `statQ38` CHAR(10) NOT NULL AFTER `statQ28`,
87 | Comal | Pekalongan 1 | D23 | Q38 | VOLTAGE 150/PEKALONGAN 1 | statQ38 | D23CTRL/XSWI4.Pos.stVal |  | ADD `DATABASE` CHAR(10) NOT NULL AFTER `statQ38`,

## Trafo 1
No | Gardu Induk | Bay | IED | HMI | POINT | Database |  | Type | " | ADD | TEXT NOT NULL AFTER | `
46 | Comal | Trafo 1 | D34 | BCU FAIL | BCU_TRAFO1_BCU_FAIL |  | D34CTRL/GGIO20.Ind7.stVal | Boolean
47 | Comal | Trafo 1 | D34 | ETHERNET FAIL TRAFO 1 CONTROL PANEL | BCU_TRAFO1_U11_FAIL |  | D34CTRL/GGIO20.Ind8.stVal | Boolean | ADD `BCU_TRAFO1_U11_FAIL` TEXT NOT NULL AFTER `BCU_TRAFO1_BCU_FAIL`, |  |  |  | "D34CTRL/GGIO20.Ind8.stVal", //BCU_TRAFO1_U11_FAIL
16 | Comal | Trafo 1 | D36 | OLS Operate | BCU_OLS_TRAFO-1 |  | D36CTRL/GGIO29.Ind6.stVal | Boolean | ADD `BCU_OLS_TRAFO-1` TEXT NOT NULL AFTER `BCU_TRAFO1_U11_FAIL`, |  |  |  | "D36CTRL/GGIO29.Ind6.stVal", //BCU_OLS_TRAFO-1
1 | Comal | Trafo 1 | D37 | Differential Operated | F87T_87T.Op_Biased |  | D37PROT/PDIF2.Op.general | Boolean | ADD `F87T_87T.Op_Biased` TEXT NOT NULL AFTER `BCU_OLS_TRAFO-1`, |  |  |  | "D37PROT/PDIF2.Op.general", //F87T_87T.Op_Biased
2 | Comal | Trafo 1 | D37 | Differetial Inst Operated | F87T_87T.Op_Inst |  | D37PROT/PDIF1.Op.general | Boolean | ADD `F87T_87T.Op_Inst` TEXT NOT NULL AFTER `F87T_87T.Op_Biased`, |  |  |  | "D37PROT/PDIF1.Op.general", //F87T_87T.Op_Inst
3 | Comal | Trafo 1 | D37 | REV HV Operated | F87T_HVS.64REF.Op |  | D37PROT/PDIF4.Op.general | Boolean | ADD `F87T_HVS.64REF.Op` TEXT NOT NULL AFTER `F87T_87T.Op_Inst`, |  |  |  | "D37PROT/PDIF4.Op.general", //F87T_HVS.64REF.Op
4 | Comal | Trafo 1 | D37 | REV LV Operated | F87T_LVS.64REF.Op |  | D37PROT/PDIF6.Op.general | Boolean | ADD `F87T_LVS.64REF.Op` TEXT NOT NULL AFTER `F87T_HVS.64REF.Op`, |  |  |  | "D37PROT/PDIF6.Op.general", //F87T_LVS.64REF.Op
5 | Comal | Trafo 1 | D37 | 87T Inrush | F87T_87T.Inrush_Current_Flag |  | D37PROT/PHAR1.Op.general | Boolean | ADD `F87T_87T.Inrush_Current_Flag` TEXT NOT NULL AFTER `F87T_LVS.64REF.Op`, |  |  |  | "D37PROT/PHAR1.Op.general", //F87T_87T.Inrush_Current_Flag
17 | Comal | Trafo 1 | D37 | Trafo 1 PH R | Trafo 1 PH R |  | D37PROT/PTRC1.Tr.phsA | Boolean | ADD `Trafo 1 PH R` TEXT NOT NULL AFTER `F87T_87T.Inrush_Current_Flag`, |  |  |  | "D37PROT/PTRC1.Tr.phsA", //Trafo 1 PH R
18 | Comal | Trafo 1 | D37 | Trafo 1 PH R | Trafo 1 PH R |  | D37PROT/PDIF2.Op.phsA |  | ADD `Trafo 1 PH R` TEXT NOT NULL AFTER `Trafo 1 PH R`, |  |  |  | "D37PROT/PDIF2.Op.phsA", //Trafo 1 PH R
19 | Comal | Trafo 1 | D37 | Trafo 1 PH R | Trafo 1 PH R |  | D37PROT/PDIF4.Op.phsA |  | ADD `Trafo 1 PH R` TEXT NOT NULL AFTER `Trafo 1 PH R`, |  |  |  | "D37PROT/PDIF4.Op.phsA", //Trafo 1 PH R
20 | Comal | Trafo 1 | D37 | Trafo 1 PH R | Trafo 1 PH R |  | D37PROT/PDIF6.Op.phsA |  | ADD `Trafo 1 PH R` TEXT NOT NULL AFTER `Trafo 1 PH R`, |  |  |  | "D37PROT/PDIF6.Op.phsA", //Trafo 1 PH R
21 | Comal | Trafo 1 | D37 | Trafo 1 PH R | Trafo 1 PH R |  | D37PROT/PDIF1.Op.phsA |  | ADD `Trafo 1 PH R` TEXT NOT NULL AFTER `Trafo 1 PH R`, |  |  |  | "D37PROT/PDIF1.Op.phsA", //Trafo 1 PH R
24 | Comal | Trafo 1 | D37 | Trafo 1 PH S | Trafo 1 PH S |  | D37PROT/PTRC1.Tr.phsB | Boolean | ADD `Trafo 1 PH S` TEXT NOT NULL AFTER `Trafo 1 PH R`, |  |  |  | "D37PROT/PTRC1.Tr.phsB", //Trafo 1 PH S
25 | Comal | Trafo 1 | D37 | Trafo 1 PH S | Trafo 1 PH S |  | D37PROT/PDIF2.Op.phsB |  | ADD `Trafo 1 PH S` TEXT NOT NULL AFTER `Trafo 1 PH S`, |  |  |  | "D37PROT/PDIF2.Op.phsB", //Trafo 1 PH S
26 | Comal | Trafo 1 | D37 | Trafo 1 PH S | Trafo 1 PH S |  | D37PROT/PDIF4.Op.phsB |  | ADD `Trafo 1 PH S` TEXT NOT NULL AFTER `Trafo 1 PH S`, |  |  |  | "D37PROT/PDIF4.Op.phsB", //Trafo 1 PH S
27 | Comal | Trafo 1 | D37 | Trafo 1 PH S | Trafo 1 PH S |  | D37PROT/PDIF6.Op.phsB |  | ADD `Trafo 1 PH S` TEXT NOT NULL AFTER `Trafo 1 PH S`, |  |  |  | "D37PROT/PDIF6.Op.phsB", //Trafo 1 PH S
28 | Comal | Trafo 1 | D37 | Trafo 1 PH S | Trafo 1 PH S |  | D37PROT/PDIF1.Op.phsB |  | ADD `Trafo 1 PH S` TEXT NOT NULL AFTER `Trafo 1 PH S`, |  |  |  | "D37PROT/PDIF1.Op.phsB", //Trafo 1 PH S
31 | Comal | Trafo 1 | D37 | Trafo 1 PH T | Trafo 1 PH T |  | D37PROT/PTRC1.Tr.phsC | Boolean
32 | Comal | Trafo 1 | D37 | Trafo 1 PH T | Trafo 1 PH T |  | D37PROT/PDIF2.Op.phsC
33 | Comal | Trafo 1 | D37 | Trafo 1 PH T | Trafo 1 PH T |  | D37PROT/PDIF4.Op.phsC
34 | Comal | Trafo 1 | D37 | Trafo 1 PH T | Trafo 1 PH T |  | D37PROT/PDIF6.Op.phsC
35 | Comal | Trafo 1 | D37 | Trafo 1 PH T | Trafo 1 PH T |  | D37PROT/PDIF1.Op.phsC
6 | Comal | Trafo 1 | D38 | OCR HV Operated | F501_50/51P4.Op |  | D38PROT/PTOC4.Op.general | Boolean
7 | Comal | Trafo 1 | D38 | OCR HV High SET 1 Operated | F501_50/51P1.Op |  | D38PROT/PTOC1.Op.general | Boolean | ADD `F501_50/51P1.Op` TEXT NOT NULL AFTER `Trafo 1 PH S`, |  |  |  | "D38PROT/PTOC1.Op.general", //F501_50/51P1.Op
8 | Comal | Trafo 1 | D38 | GFR Operated | F501_50/51G4.Op |  | D38PROT/PTOC8.Op.general | Boolean
9 | Comal | Trafo 1 | D38 | F501 100% Load | F501_50/51P3.Op |  | D38PROT/PTOC7.Op.general | Boolean
22 | Comal | Trafo 1 | D38 | Trafo 1 PH R | Trafo 1 PH R |  | D38PROT/PTRC1.Op.phsA
29 | Comal | Trafo 1 | D38 | Trafo 1 PH S | Trafo 1 PH S |  | D38PROT/PTRC1.Op.phsB
36 | Comal | Trafo 1 | D38 | Trafo 1 PH T | Trafo 1 PH T |  | D38PROT/PTRC1.Op.phsC
10 | Comal | Trafo 1 | D39 | OCR LV Operated | F502_50/51G4.Op |  | D39PROT/PTOC8.Op.phsC | Boolean
11 | Comal | Trafo 1 | D39 | OCR LV High SET 1 Operated | F502_50/51P1.Op |  | D39PROT/PTOC1.Op.phsC | Boolean | ADD `F502_50/51P1.Op` TEXT NOT NULL AFTER `F501_50/51P1.Op`, |  |  |  | "D39PROT/PTOC1.Op.phsC", //F502_50/51P1.Op
12 | Comal | Trafo 1 | D39 | OCR LV High SET 2 Operated | F502_50/51P2.Op |  | D39PROT/PTOC2.Op.phsC | Boolean
13 | Comal | Trafo 1 | D39 | GFR LV Operated | F502_50/51G4.Op |  | D39PROT/PTOC8.Op.phsC | Boolean
14 | Comal | Trafo 1 | D39 | GFR LV High SET 1 Operated | F502_50/51G1.Op |  | D39PROT/PTOC5.Op.phsC | Boolean
15 | Comal | Trafo 1 | D39 | GFR LV High SET 2 Operated | F502_50/51G2.Op |  | D39PROT/PTOC6.Op.phsC | Boolean
23 | Comal | Trafo 1 | D39 | Trafo 1 PH R | Trafo 1 PH R |  | D39PROT/PTRC1.Op.phsA
30 | Comal | Trafo 1 | D39 | Trafo 1 PH S | Trafo 1 PH S |  | D39PROT/PTRC1.Op.phsB
37 | Comal | Trafo 1 | D39 | Trafo 1 PH T | Trafo 1 PH T |  | D39PROT/PTRC1.Op.phsC |  | ADD `Trafo 1 PH T` TEXT NOT NULL AFTER `F502_50/51P1.Op`, |  |  |  | "D39PROT/PTRC1.Op.phsC", //Trafo 1 PH T
38 | Comal | Trafo 1 | D39 | 20kV CB Incoming In Test | F502_20KV_CB_INCOMING_IN_TEST |  | D39PROT/GGIO10.Ind4.stVal | Boolean | ADD `F502_20KV_CB_INCOMING_IN_TEST` TEXT NOT NULL AFTER `Trafo 1 PH T`, |  |  |  | "D39PROT/GGIO10.Ind4.stVal", //F502_20KV_CB_INCOMING_IN_TEST
39 | Comal | Trafo 1 | D39 | 20kV CB Incoming In Service | F502_20KV_CB_INCOMING_IN_SERVICE |  | D39PROT/GGIO10.Ind5.stVal | Boolean | ADD `F502_20KV_CB_INCOMING_IN_SERVICE` TEXT NOT NULL AFTER `F502_20KV_CB_INCOMING_IN_TEST`, |  |  |  | "D39PROT/GGIO10.Ind5.stVal", //F502_20KV_CB_INCOMING_IN_SERVICE
40 | Comal | Trafo 1 | D39 | Motor Supply Fail | F502_MOTOR_SUPPLY_FAIL |  | D39PROT/GGIO10.Ind6.stVal | Boolean | ADD `F502_MOTOR_SUPPLY_FAIL` TEXT NOT NULL AFTER `F502_20KV_CB_INCOMING_IN_SERVICE`, |  |  |  | "D39PROT/GGIO10.Ind6.stVal", //F502_MOTOR_SUPPLY_FAIL
41 | Comal | Trafo 1 | D39 | Control Supply Fail | F502_CONTROL_SUPPLY_FAIL |  | D39PROT/GGIO10.Ind7.stVal | Boolean | ADD `F502_CONTROL_SUPPLY_FAIL` TEXT NOT NULL AFTER `F502_MOTOR_SUPPLY_FAIL`, |  |  |  | "D39PROT/GGIO10.Ind7.stVal", //F502_CONTROL_SUPPLY_FAIL
42 | Comal | Trafo 1 | D39 | 20kV Incoming Switch Local | F502_20KV_INCOMING_SWITCH_LOCAL |  | D39PROT/GGIO10.Ind8.stVal | Boolean | ADD `F502_20KV_INCOMING_SWITCH_LOCAL` TEXT NOT NULL AFTER `F502_CONTROL_SUPPLY_FAIL`, |  |  |  | "D39PROT/GGIO10.Ind8.stVal", //F502_20KV_INCOMING_SWITCH_LOCAL
43 | Comal | Trafo 1 | D39 | 20kV Incoming Switch Remote | F502_20KV_INCOMING_SWITCH_REMOTE |  | D39PROT/GGIO11.Ind1.stVal | Boolean | ADD `F502_20KV_INCOMING_SWITCH_REMOTE` TEXT NOT NULL AFTER `F502_20KV_INCOMING_SWITCH_LOCAL`, |  |  |  | "D39PROT/GGIO11.Ind1.stVal", //F502_20KV_INCOMING_SWITCH_REMOTE
44 | Comal | Trafo 1 | D39 | Tripping Supply Fail | F502_TRIPPING_SUPPLY_FAIL |  | D39PROT/GGIO11.Ind3.stVal | Boolean | ADD `F502_TRIPPING_SUPPLY_FAIL` TEXT NOT NULL AFTER `F502_20KV_INCOMING_SWITCH_REMOTE`, |  |  |  | "D39PROT/GGIO11.Ind3.stVal", //F502_TRIPPING_SUPPLY_FAIL
45 | Comal | Trafo 1 | D39 | VT MCB Fault Trip | F502_VT_MCB_FAULT_TRIP |  | D39PROT/GGIO11.Ind4.stVal | Boolean | ADD `F502_VT_MCB_FAULT_TRIP` TEXT NOT NULL AFTER `F502_TRIPPING_SUPPLY_FAIL`, |  |  |  | "D39PROT/GGIO11.Ind4.stVal", //F502_VT_MCB_FAULT_TRIP
48 | Comal | Trafo 1 | D40 | ETHERNET FAIL TRAFO 1 PROT PANEL | BCU_ETHERNET_FAIL_TRAFO_1_PROT_PANEL |  | D40PROT/GGIO19.Ind7.stVal | Boolean | ADD `BCU_ETHERNET_FAIL_TRAFO_1_PROT_PANEL` TEXT NOT NULL AFTER `F502_VT_MCB_FAULT_TRIP`, |  |  |  | "D40PROT/GGIO19.Ind7.stVal", //BCU_ETHERNET_FAIL_TRAFO_1_PROT_PANEL
49 | Comal | Trafo 1 | D40 | F87T FAIL | BCU_F87T_FAIL |  | D40PROT/GGIO19.Ind1.stVal | Boolean | ADD `BCU_F87T_FAIL` TEXT NOT NULL AFTER `BCU_ETHERNET_FAIL_TRAFO_1_PROT_PANEL`, |  |  |  | "D40PROT/GGIO19.Ind1.stVal", //BCU_F87T_FAIL
50 | Comal | Trafo 1 | D40 | F501 FAIL | BCU_F501_FAIL |  | D40PROT/GGIO19.Ind3.stVal | Boolean | ADD `BCU_F501_FAIL` TEXT NOT NULL AFTER `BCU_F87T_FAIL`, |  |  |  | "D40PROT/GGIO19.Ind3.stVal", //BCU_F501_FAIL
51 | Comal | Trafo 1 | D40 | F502 FAIL | BCU_F502_FAIL |  | D40PROT/GGIO19.Ind5.stVal | Boolean | ADD `BCU_F502_FAIL` TEXT NOT NULL AFTER `BCU_F501_FAIL`, |  |  |  | "D40PROT/GGIO19.Ind5.stVal", //BCU_F502_FAIL
52 | Comal | Trafo 1 | D40 | SF6 STAGE 2 BLOCK | BCU_SF6 STAGE 2 BLOCK |  | D40CTRL/GGIO28.Ind1.stVal | Boolean | ADD `BCU_SF6 STAGE 2 BLOCK` TEXT NOT NULL AFTER `BCU_F502_FAIL`, |  |  |  | "D40CTRL/GGIO28.Ind1.stVal", //BCU_SF6 STAGE 2 BLOCK
53 | Comal | Trafo 1 | D40 | SF6 STAGE 1 ALARM | BCU_SF6 STAGE 1 ALARM |  | D40CTRL/GGIO28.Ind3.stVal | Boolean | ADD `BCU_SF6 STAGE 1 ALARM` TEXT NOT NULL AFTER `BCU_SF6 STAGE 2 BLOCK`, |  |  |  | "D40CTRL/GGIO28.Ind3.stVal", //BCU_SF6 STAGE 1 ALARM
54 | Comal | Trafo 1 | D40 | CLOSE SPRING UNCHARGE | BCU_CLOSE_SPRG_UNCHRG |  | D40CTRL/GGIO28.Ind4.stVal | Boolean | ADD `BCU_CLOSE_SPRG_UNCHRG` TEXT NOT NULL AFTER `BCU_SF6 STAGE 1 ALARM`, |  |  |  | "D40CTRL/GGIO28.Ind4.stVal", //BCU_CLOSE_SPRG_UNCHRG
55 | Comal | Trafo 1 | D40 | CB Q0 MOTOR MCB TRIP | BCU_CB_Q0_MTR_MCB_TRIP |  | D40CTRL/GGIO28.Ind5.stVal | Boolean | ADD `BCU_CB_Q0_MTR_MCB_TRIP` TEXT NOT NULL AFTER `BCU_CLOSE_SPRG_UNCHRG`, |  |  |  | "D40CTRL/GGIO28.Ind5.stVal", //BCU_CB_Q0_MTR_MCB_TRIP
56 | Comal | Trafo 1 | D40 | DS Q1 MOTOR MCB TRIP | BCU_DS_Q1_MTR_MCB_TRIP |  | D40CTRL/GGIO29.Ind3.stVal | Boolean | ADD `BCU_DS_Q1_MTR_MCB_TRIP` TEXT NOT NULL AFTER `BCU_CB_Q0_MTR_MCB_TRIP`, |  |  |  | "D40CTRL/GGIO29.Ind3.stVal", //BCU_DS_Q1_MTR_MCB_TRIP
57 | Comal | Trafo 1 | D40 | DS Q1 CONTROL MCB TRIP | BCU_DS_Q1_CTRL_MCB_TRIP |  | D40CTRL/GGIO29.Ind4.stVal | Boolean | ADD `BCU_DS_Q1_CTRL_MCB_TRIP` TEXT NOT NULL AFTER `BCU_DS_Q1_MTR_MCB_TRIP`, |  |  |  | "D40CTRL/GGIO29.Ind4.stVal", //BCU_DS_Q1_CTRL_MCB_TRIP
58 | Comal | Trafo 1 | D40 | DS Q2 MOTOR MCB TRIP | BCU_DS_Q2_MTR_MCB_TRIP |  | D40CTRL/GGIO30.Ind2.stVal | Boolean | ADD `BCU_DS_Q2_MTR_MCB_TRIP` TEXT NOT NULL AFTER `BCU_DS_Q1_CTRL_MCB_TRIP`, |  |  |  | "D40CTRL/GGIO30.Ind2.stVal", //BCU_DS_Q2_MTR_MCB_TRIP
59 | Comal | Trafo 1 | D40 | DS Q2 CONTROL MCB TRIP | BCU_DS_Q2_CTRL_MCB_TRIP |  | D40CTRL/GGIO30.Ind3.stVal | Boolean | ADD `BCU_DS_Q2_CTRL_MCB_TRIP` TEXT NOT NULL AFTER `BCU_DS_Q2_MTR_MCB_TRIP`, |  |  |  | "D40CTRL/GGIO30.Ind3.stVal", //BCU_DS_Q2_CTRL_MCB_TRIP
60 | Comal | Trafo 1 | D40 | MCB AC TRIP | BCU_B07.BI_15 |  | D40CTRL/GGIO17.Ind7.stVal | Boolean | ADD `BCU_B07.BI_15` TEXT NOT NULL AFTER `BCU_DS_Q2_CTRL_MCB_TRIP`, |  |  |  | "D40CTRL/GGIO17.Ind7.stVal", //BCU_B07.BI_15
61 | Comal | Trafo 1 | D40 | MAIN TANK OIL HIGH LEVEL ALARM | BCU_M_TANK_OIL_HIGH_LVL_ALARM |  | D40CTRL/GGIO31.Ind1.stVal | Boolean | ADD `BCU_M_TANK_OIL_HIGH_LVL_ALARM` TEXT NOT NULL AFTER `BCU_B07.BI_15`, |  |  |  | "D40CTRL/GGIO31.Ind1.stVal", //BCU_M_TANK_OIL_HIGH_LVL_ALARM
62 | Comal | Trafo 1 | D40 | OLTC OIL HIGH LEVEL ALARM | BCU_OLTC_OIL_HIGH_LVL_ALARM |  | D40CTRL/GGIO31.Ind2.stVal | Boolean | ADD `BCU_OLTC_OIL_HIGH_LVL_ALARM` TEXT NOT NULL AFTER `BCU_M_TANK_OIL_HIGH_LVL_ALARM`, |  |  |  | "D40CTRL/GGIO31.Ind2.stVal", //BCU_OLTC_OIL_HIGH_LVL_ALARM
63 | Comal | Trafo 1 | D40 | BUCHOLZ ALARM | BUCHOLZ_ALARM |  | D40CTRL/GGIO31.Ind3.stVal | Boolean | ADD `BUCHOLZ_ALARM` TEXT NOT NULL AFTER `BCU_OLTC_OIL_HIGH_LVL_ALARM`, |  |  |  | "D40CTRL/GGIO31.Ind3.stVal", //BUCHOLZ_ALARM
64 | Comal | Trafo 1 | D40 | OIL TEMP ALARM | OIL_TEMP_ALARM |  | D40CTRL/GGIO31.Ind4.stVal | Boolean | ADD `OIL_TEMP_ALARM` TEXT NOT NULL AFTER `BUCHOLZ_ALARM`, |  |  |  | "D40CTRL/GGIO31.Ind4.stVal", //OIL_TEMP_ALARM
65 | Comal | Trafo 1 | D40 | MAIN TANK BREATH CONSV. ALARM | MT_BREATH_CONSV_ALARM |  | D40CTRL/GGIO31.Ind5.stVal | Boolean | ADD `MT_BREATH_CONSV_ALARM` TEXT NOT NULL AFTER `OIL_TEMP_ALARM`, |  |  |  | "D40CTRL/GGIO31.Ind5.stVal", //MT_BREATH_CONSV_ALARM
66 | Comal | Trafo 1 | D40 | OLTC BREATH CONSV. ALARM | OLTC_BREATH_CONSV_ALARM |  | D40CTRL/GGIO31.Ind6.stVal | Boolean | ADD `OLTC_BREATH_CONSV_ALARM` TEXT NOT NULL AFTER `MT_BREATH_CONSV_ALARM`, |  |  |  | "D40CTRL/GGIO31.Ind6.stVal", //OLTC_BREATH_CONSV_ALARM
67 | Comal | Trafo 1 | D40 | LV WINDING TEMP. ALARM | LV_WIND_TEMP_ALARM |  | D40CTRL/GGIO31.Ind7.stVal | Boolean | ADD `LV_WIND_TEMP_ALARM` TEXT NOT NULL AFTER `OLTC_BREATH_CONSV_ALARM`, |  |  |  | "D40CTRL/GGIO31.Ind7.stVal", //LV_WIND_TEMP_ALARM
68 | Comal | Trafo 1 | D40 | HV WINDING TEMPT. ALARM | HV_WIND_TEMP_ALARM |  | D40CTRL/GGIO31.Ind8.stVal | Boolean | ADD `HV_WIND_TEMP_ALARM` TEXT NOT NULL AFTER `LV_WIND_TEMP_ALARM`, |  |  |  | "D40CTRL/GGIO31.Ind8.stVal", //HV_WIND_TEMP_ALARM
69 | Comal | Trafo 1 | D40 | COOLING FAN FAIL | COOLING_FAN_FAIL |  | D40CTRL/GGIO32.Ind1.stVal | Boolean | ADD `COOLING_FAN_FAIL` TEXT NOT NULL AFTER `HV_WIND_TEMP_ALARM`, |  |  |  | "D40CTRL/GGIO32.Ind1.stVal", //COOLING_FAN_FAIL
70 | Comal | Trafo 1 | D40 | OLTC MOTOR RDRIVE FAIL | OLTC_MOTOR_DRIVE_FAIL |  | D40CTRL/GGIO32.Ind2.stVal | Boolean | ADD `OLTC_MOTOR_DRIVE_FAIL` TEXT NOT NULL AFTER `COOLING_FAN_FAIL`, |  |  |  | "D40CTRL/GGIO32.Ind2.stVal", //OLTC_MOTOR_DRIVE_FAIL
71 | Comal | Trafo 1 | D40 | TCS 1 FAIL | TCS1_FAIL |  | D40CTRL/GGIO20.Ind6.stVal | Boolean | ADD `TCS1_FAIL` TEXT NOT NULL AFTER `OLTC_MOTOR_DRIVE_FAIL`, |  |  |  | "D40CTRL/GGIO20.Ind6.stVal", //TCS1_FAIL
72 | Comal | Trafo 1 | D40 | TCS 2 FAIL | TCS2_FAIL |  | D40CTRL/GGIO20.Ind7.stVal |  | ADD `TCS2_FAIL` TEXT NOT NULL AFTER `TCS1_FAIL`, |  |  |  | "D40CTRL/GGIO20.Ind7.stVal", //TCS2_FAIL
73 | Comal | Trafo 1 | D40 | K861 OPERATE | K861_TRIP |  | D40CTRL/GGIO19.Ind8.stVal
74 | Comal | Trafo 1 | D40 | K862 OPERATE | K862_TRIP |  | D40CTRL/GGIO20.Ind2.stVal
75 | Comal | Trafo 1 | D40 | K863 OPERATE | K863_TRIP |  | D40CTRL/GGIO20.Ind4.stVal
76 | Comal | Trafo 1 | D40 | MK MCB HEATER TRIP | BCU_B12.BI_20 |  | D40CTRL/GGIO33.Ind4.stVal
77 | Comal | Trafo 1 | D40 | BUCHLOZ TRIP | BUCHOLZ_TRIP |  | D40CTRL/GGIO20.Ind8.stVal
78 | Comal | Trafo 1 | D40 | OIL TEMP. TRIP | OIL_TEMP_TRIP |  | D40CTRL/GGIO21.Ind1.stVal |  | =?,
79 | Comal | Trafo 1 | D40 | HV WINDING TEMPT. TRIP | HV_WIND_TEMP_TRIP |  | D40CTRL/GGIO21.Ind2.stVal
80 | Comal | Trafo 1 | D40 | PROTECTION POWER FAIL | PROT_POWER_FAIL |  | D40CTRL/GGIO21.Ind3.stVal |  | BCU_TRAFO1_U11_FAIL=?,
81 | Comal | Trafo 1 | D40 | CONTROL POWER FAIL | CTRL_POWER_FAIL |  | D40CTRL/GGIO21.Ind4.stVal |  | BCU_OLS_TRAFO-1=?,
82 | Comal | Trafo 1 | D40 | MCB AUX DDC SUPPLY FAIL | MCB_AUX_DC_SUPPLY_FAIL |  | D40CTRL/GGIO21.Ind5.stVal |  | F87T_87T.Op_Biased=?,
83 | Comal | Trafo 1 | D40 | LV WINDING TEMPT. TRIP | LV_WIND_TEMP_TRIP |  | D40CTRL/GGIO22.Ind1.stVal |  | F87T_87T.Op_Inst=?,
84 | Comal | Trafo 1 | D40 | PRESSURE RELIEFE TRIP | PRESS_RELIEF_TRIP |  | D40CTRL/GGIO22.Ind2.stVal |  | F87T_HVS.64REF.Op=?,
85 | Comal | Trafo 1 | D40 | OLTC PRESSURE RELIEFE TRIP | OLTC_PRESS_RELIEF_TRIP |  | D40CTRL/GGIO22.Ind3.stVal |  | F87T_LVS.64REF.Op=?,
86 | Comal | Trafo 1 | D40 | JANSEN RELAY TRIP | JANSEN RELAY TRIP |  | D40CTRL/GGIO22.Ind4.stVal |  | F87T_87T.Inrush_Current_Flag=?,
87 | Comal | Trafo 1 | D40 | MAIN TANK OIL LEVEL LOW | M_TANK_OIL_LVL_LOW |  | D40CTRL/GGIO22.Ind5.stVal |  | Trafo 1 PH R=?,
88 | Comal | Trafo 1 | D40 | OLTC OIL LEVEL LOW | OLTC_OIL_LVL_LOW |  | D40CTRL/GGIO22.Ind6.stVal |  | Trafo 1 PH R=?,
89 | Comal | Trafo 1 | D40 | MK MOTOR MCB TRIP | MOTOR_MCB_TRIP |  | D40CTRL/GGIO23.Ind4.stVal |  | Trafo 1 PH R=?,
Trafo 1 PH R=?,
Trafo 1 PH R=?,
Trafo 1 PH S=?,
Trafo 1 PH S=?,
Trafo 1 PH S=?,
Trafo 1 PH S=?,
Trafo 1 PH S=?,
F501_50/51P1.Op=?,
F502_50/51P1.Op=?,
Trafo 1 PH T=?,
F502_20KV_CB_INCOMING_IN_TEST=?,
F502_20KV_CB_INCOMING_IN_SERVICE=?,
F502_MOTOR_SUPPLY_FAIL=?,
F502_CONTROL_SUPPLY_FAIL=?,
F502_20KV_INCOMING_SWITCH_LOCAL=?,
F502_20KV_INCOMING_SWITCH_REMOTE=?,
F502_TRIPPING_SUPPLY_FAIL=?,
F502_VT_MCB_FAULT_TRIP=?,
BCU_ETHERNET_FAIL_TRAFO_1_PROT_PANEL=?,
BCU_F87T_FAIL=?,
BCU_F501_FAIL=?,
BCU_F502_FAIL=?,
BCU_SF6 STAGE 2 BLOCK=?,
BCU_SF6 STAGE 1 ALARM=?,
BCU_CLOSE_SPRG_UNCHRG=?,
BCU_CB_Q0_MTR_MCB_TRIP=?,
BCU_DS_Q1_MTR_MCB_TRIP=?,
BCU_DS_Q1_CTRL_MCB_TRIP=?,
BCU_DS_Q2_MTR_MCB_TRIP=?,
BCU_DS_Q2_CTRL_MCB_TRIP=?,
BCU_B07.BI_15=?,
BCU_M_TANK_OIL_HIGH_LVL_ALARM=?,
BCU_OLTC_OIL_HIGH_LVL_ALARM=?,
BUCHOLZ_ALARM=?,
OIL_TEMP_ALARM=?,
MT_BREATH_CONSV_ALARM=?,
OLTC_BREATH_CONSV_ALARM=?,
LV_WIND_TEMP_ALARM=?,
HV_WIND_TEMP_ALARM=?,
COOLING_FAN_FAIL=?,
OLTC_MOTOR_DRIVE_FAIL=?,
TCS1_FAIL=?,
TCS2_FAIL=?,

## Kopel
No | Gardu Induk | Bay | IED | HMI | SCE | Database |  | Type | " | ADD | TEXT NOT NULL AFTER | `
1 | Pekalongan | Kopel | D32 | BCU FAIL | BCU_BCU_BCPL_FAIL |  |  | Boolean | ADD `BCU_BCU_BCPL_FAIL` TEXT NOT NULL AFTER `SCE`, |  |  |  | "", //BCU_BCU_BCPL_FAIL
2 | Pekalongan | Kopel | D32 | ETHERNET FAIL | BCU_ETHERNET_BCPL_FAIL |  |  | Boolean | ADD `BCU_ETHERNET_BCPL_FAIL` TEXT NOT NULL AFTER `BCU_BCU_BCPL_FAIL`, |  |  |  | "", //BCU_ETHERNET_BCPL_FAIL
3 | Pekalongan | Kopel | D34 | SF6 STAGE 2 BLOCK | BCU_SF6_SF6 STAGE 2 BLOCK |  | D34CTRL/GGIO28.Ind2.stVal | Boolean | ADD `BCU_SF6_SF6 STAGE 2 BLOCK` TEXT NOT NULL AFTER `BCU_ETHERNET_BCPL_FAIL`, |  |  |  | "D34CTRL/GGIO28.Ind2.stVal", //BCU_SF6_SF6 STAGE 2 BLOCK
4 | Pekalongan | Kopel | D34 | SF6 STAGE 1 ALARM | BCU_SF6_STAGE_1_ALARM |  | D34CTRL/GGIO28.Ind3.stVal | Boolean | ADD `BCU_SF6_STAGE_1_ALARM` TEXT NOT NULL AFTER `BCU_SF6_SF6 STAGE 2 BLOCK`, |  |  |  | "D34CTRL/GGIO28.Ind3.stVal", //BCU_SF6_STAGE_1_ALARM
5 | Pekalongan | Kopel | D34 | CLOSE SPRING UNCHARGE | BCU_CLOSE_SPRING_UNCHARGE |  | D34CTRL/GGIO28.Ind4.stVal | Boolean | ADD `BCU_CLOSE_SPRING_UNCHARGE` TEXT NOT NULL AFTER `BCU_SF6_STAGE_1_ALARM`, |  |  |  | "D34CTRL/GGIO28.Ind4.stVal", //BCU_CLOSE_SPRING_UNCHARGE
6 | Pekalongan | Kopel | D34 | MOTOR MCB TRIP | BCU_MOTOR_MCB_TRIP |  | D34CTRL/GGIO28.Ind5.stVal | Boolean | ADD `BCU_MOTOR_MCB_TRIP` TEXT NOT NULL AFTER `BCU_CLOSE_SPRING_UNCHARGE`, |  |  |  | "D34CTRL/GGIO28.Ind5.stVal", //BCU_MOTOR_MCB_TRIP
7 | Pekalongan | Kopel | D34 | DS Q1 MOTOR MCB TRIP | BCU_DS_Q1_MOTOR_MCB_TRIP |  | D34CTRL/GGIO29.Ind3.stVal | Boolean | ADD `BCU_DS_Q1_MOTOR_MCB_TRIP` TEXT NOT NULL AFTER `BCU_MOTOR_MCB_TRIP`, |  |  |  | "D34CTRL/GGIO29.Ind3.stVal", //BCU_DS_Q1_MOTOR_MCB_TRIP
8 | Pekalongan | Kopel | D34 | DS Q1 CONTROL MCB TRIP | BCU_DS_Q1_CONTROL_MCB_TRIP |  | D34CTRL/GGIO29.Ind4.stVal | Boolean | ADD `BCU_DS_Q1_CONTROL_MCB_TRIP` TEXT NOT NULL AFTER `BCU_DS_Q1_MOTOR_MCB_TRIP`, |  |  |  | "D34CTRL/GGIO29.Ind4.stVal", //BCU_DS_Q1_CONTROL_MCB_TRIP
9 | Pekalongan | Kopel | D34 | DS Q2 MOTOR MCB TRIP | BCU_DS_Q2_MOTOR_MCB_TRIP |  | D34CTRL/GGIO30.Ind2.stVal | Boolean | ADD `BCU_DS_Q2_MOTOR_MCB_TRIP` TEXT NOT NULL AFTER `BCU_DS_Q1_CONTROL_MCB_TRIP`, |  |  |  | "D34CTRL/GGIO30.Ind2.stVal", //BCU_DS_Q2_MOTOR_MCB_TRIP
10 | Pekalongan | Kopel | D34 | DS Q2 CONTROL MCB TRIP | BCU_DS_Q2_CONTROL_MCB_TRIP |  | D34CTRL/GGIO30.Ind3.stVal | Boolean | ADD `BCU_DS_Q2_CONTROL_MCB_TRIP` TEXT NOT NULL AFTER `BCU_DS_Q2_MOTOR_MCB_TRIP`, |  |  |  | "D34CTRL/GGIO30.Ind3.stVal", //BCU_DS_Q2_CONTROL_MCB_TRIP
11 | Pekalongan | Kopel | D34 | MCB AC TRIP | BCU_B07.BI_13 |  | D34CTRL/GGIO17.Ind5.stVal | Boolean | ADD `BCU_B07.BI_13` TEXT NOT NULL AFTER `BCU_DS_Q2_CONTROL_MCB_TRIP`, |  |  |  | "D34CTRL/GGIO17.Ind5.stVal", //BCU_B07.BI_13
12 | Pekalongan | Kopel | D34 | F51 FAIL | BCU_F51_FAIL |  | D34CTRL/GGIO17.Ind8.stVal | Boolean | ADD `BCU_F51_FAIL` TEXT NOT NULL AFTER `BCU_B07.BI_13`, |  |  |  | "D34CTRL/GGIO17.Ind8.stVal", //BCU_F51_FAIL
13 | Pekalongan | Kopel | D34 | F51 ALARM | BCU_F51_ALARM |  | D34CTRL/GGIO18.Ind1.stVal | Boolean | ADD `BCU_F51_ALARM` TEXT NOT NULL AFTER `BCU_F51_FAIL`, |  |  |  | "D34CTRL/GGIO18.Ind1.stVal", //BCU_F51_ALARM
14 | Pekalongan | Kopel | D34 | TCS 1 FAIL | BCU_TCS_1_FAIL |  | D34CTRL/GGIO18.Ind5.stVal | Boolean | ADD `BCU_TCS_1_FAIL` TEXT NOT NULL AFTER `BCU_F51_ALARM`, |  |  |  | "D34CTRL/GGIO18.Ind5.stVal", //BCU_TCS_1_FAIL
15 | Pekalongan | Kopel | D34 | TCS 2 FAIL | BCU_TCS_2_FAIL |  | D34CTRL/GGIO19.Ind1.stVal | Boolean | ADD `BCU_TCS_2_FAIL` TEXT NOT NULL AFTER `BCU_TCS_1_FAIL`, |  |  |  | "D34CTRL/GGIO19.Ind1.stVal", //BCU_TCS_2_FAIL
16 | Pekalongan | Kopel | D34 | PROTECTION SUPPLY FAIL | BCU_PROT_SUPPLY_FAIL |  | D34CTRL/GGIO21.Ind3.stVal | Boolean | ADD `BCU_PROT_SUPPLY_FAIL` TEXT NOT NULL AFTER `BCU_TCS_2_FAIL`, |  |  |  | "D34CTRL/GGIO21.Ind3.stVal", //BCU_PROT_SUPPLY_FAIL
17 | Pekalongan | Kopel | D34 | CONTROL 1 SUPPLY FAIL | BCU_CONTROL_1_SUPPLY_FAIL |  | D34CTRL/GGIO21.Ind4.stVal | Boolean | ADD `BCU_CONTROL_1_SUPPLY_FAIL` TEXT NOT NULL AFTER `BCU_PROT_SUPPLY_FAIL`, |  |  |  | "D34CTRL/GGIO21.Ind4.stVal", //BCU_CONTROL_1_SUPPLY_FAIL
18 | Pekalongan | Kopel | D34 | CONTROL 2 SUPPLY FAIL | BCU_CONTROL_2_SUPPLY_FAIL |  | D34CTRL/GGIO21.Ind5.stVal | Boolean | ADD `BCU_CONTROL_2_SUPPLY_FAIL` TEXT NOT NULL AFTER `BCU_CONTROL_1_SUPPLY_FAIL`, |  |  |  | "D34CTRL/GGIO21.Ind5.stVal", //BCU_CONTROL_2_SUPPLY_FAIL
19 | Pekalongan | Kopel | D34 | K861 OPERATED | BCU_B07.BI_10 |  | D34CTRL/GGIO17.Ind2.stVal | Boolean | ADD `BCU_B07.BI_10` TEXT NOT NULL AFTER `BCU_CONTROL_2_SUPPLY_FAIL`, |  |  |  | "D34CTRL/GGIO17.Ind2.stVal", //BCU_B07.BI_10
20 | Pekalongan | Kopel | D34 | K862 OPERATED | BCU_B07.BI_11 |  | D34CTRL/GGIO17.Ind3.stVal | Boolean | ADD `BCU_B07.BI_11` TEXT NOT NULL AFTER `BCU_B07.BI_10`, |  |  |  | "D34CTRL/GGIO17.Ind3.stVal", //BCU_B07.BI_11
21 | Pekalongan | Kopel | D34 | K863 OPERATED | BCU_B07.BI_12 |  | D34CTRL/GGIO17.Ind4.stVal | Boolean | ADD `BCU_B07.BI_12` TEXT NOT NULL AFTER `BCU_B07.BI_11`, |  |  |  | "D34CTRL/GGIO17.Ind4.stVal", //BCU_B07.BI_12
22 | Pekalongan | Kopel | D33 | OCR OPERATED | F51_50/51P3.Op |  | D33PROT/PTOC3.Op.general | Boolean | ADD `F51_50/51P3.Op` TEXT NOT NULL AFTER `BCU_B07.BI_12`, |  |  |  | "D33PROT/PTOC3.Op.general", //F51_50/51P3.Op
23 | Pekalongan | Kopel | D33 | GFR OPERATED | F51_50/51G3.Op |  | D33PROT/PTOC7.Op.general | Boolean | ADD `F51_50/51G3.Op` TEXT NOT NULL AFTER `F51_50/51P3.Op`, |  |  |  | "D33PROT/PTOC7.Op.general", //F51_50/51G3.Op
24 | Pekalongan | Kopel |  | KOPEL PH R | KOSONG |  |  | Boolean | ADD `KOSONG` TEXT NOT NULL AFTER `F51_50/51G3.Op`, |  |  |  | "", //KOSONG
25 | Pekalongan | Kopel |  | KOPEL PH S | KOSONG |  |  | Boolean | ADD `KOSONG` TEXT NOT NULL AFTER `KOSONG`, |  |  |  | "", //KOSONG
26 | Pekalongan | Kopel |  | KOPEL PH T | KOSONG |  |  | Boolean | ADD `KOSONG` TEXT NOT NULL AFTER `KOSONG`, |  |  |  | "", //KOSONG
27 | Pekalongan | Kopel | D34 |  | BCU_DS_Q1_DPOS | statQ21 | D34CTTRL/XSWI1.Pos.stVal | Boolean | ADD `BCU_DS_Q1_DPOS` TEXT NOT NULL AFTER `KOSONG`, |  |  |  | "D34CTTRL/XSWI1.Pos.stVal", //BCU_DS_Q1_DPOS
28 | Pekalongan | Kopel | D34 |  | BCU_DS_Q2_DPOS | statQ22 | D34CTTRL/XSWI2.Pos.stVal | Boolean | ADD `BCU_DS_Q2_DPOS` TEXT NOT NULL AFTER `BCU_DS_Q1_DPOS`, |  |  |  | "D34CTTRL/XSWI2.Pos.stVal", //BCU_DS_Q2_DPOS
29 | Pekalongan | Kopel | D34 |  | BCU_CB_Q0.2_DPOS | statQ50 | D34CTTRL/XCBR1.Pos.stVal | Boolean | ADD `BCU_CB_Q0.2_DPOS` TEXT NOT NULL AFTER `BCU_DS_Q2_DPOS`, |  |  |  | "D34CTTRL/XCBR1.Pos.stVal", //BCU_CB_Q0.2_DPOS
30 | Pekalongan | Kopel | [5 empty] | Boolean | ADD `` TEXT NOT NULL AFTER `BCU_CB_Q0.2_DPOS`, |  |  |  | "", //
31 | Pekalongan | Kopel | [5 empty] | Boolean | ADD `` TEXT NOT NULL AFTER ``, |  |  |  | "", //
32 | Pekalongan | Kopel | [5 empty] | Boolean | ADD `` TEXT NOT NULL AFTER ``, |  |  |  | "", //
33 | Pekalongan | Kopel | [5 empty] | Boolean | ADD `` TEXT NOT NULL AFTER ``, |  |  |  | "", //
34 | Pekalongan | Kopel | [5 empty] | Boolean | ADD `` TEXT NOT NULL AFTER ``, |  |  |  | "", //
35 | Pekalongan | Kopel | [5 empty] | Boolean | ADD `` TEXT NOT NULL AFTER ``, |  |  |  | "", //
36 | Pekalongan | Kopel | [5 empty] | Boolean | ADD `` TEXT NOT NULL AFTER ``, |  |  |  | "", //
37 | Pekalongan | Kopel | [5 empty] | Boolean | ADD `` TEXT NOT NULL AFTER ``, |  |  |  | "", //
38 | Pekalongan | Kopel | [5 empty] | Boolean | ADD `` TEXT NOT NULL AFTER ``, |  |  |  | "", //
39 | Pekalongan | Kopel | [5 empty] | Boolean | ADD `` TEXT NOT NULL AFTER ``, |  |  |  | "", //
40 | Pekalongan | Kopel | [5 empty] | Boolean | ADD `` TEXT NOT NULL AFTER ``, |  |  |  | "", //
41 | Pekalongan | Kopel | [5 empty] | Boolean | ADD `` TEXT NOT NULL AFTER ``, |  |  |  | "", //
42 | Pekalongan | Kopel | [5 empty] | Boolean | ADD `` TEXT NOT NULL AFTER ``, |  |  |  | "", //
43 | Pekalongan | Kopel | [5 empty] | Boolean | ADD `` TEXT NOT NULL AFTER ``, |  |  |  | "", //
44 | Pekalongan | Kopel | [5 empty] | Boolean | ADD `` TEXT NOT NULL AFTER ``, |  |  |  | "", //
45 | Pekalongan | Kopel | [5 empty] | Boolean | ADD `` TEXT NOT NULL AFTER ``, |  |  |  | "", //
46 | Pekalongan | Kopel | [5 empty] | Boolean | ADD `` TEXT NOT NULL AFTER ``, |  |  |  | "", //
47 | Pekalongan | Kopel | [5 empty] | Boolean | ADD `` TEXT NOT NULL AFTER ``, |  |  |  | "", //
48 | Pekalongan | Kopel | [5 empty] | Boolean | ADD `` TEXT NOT NULL AFTER ``, |  |  |  | "", //
49 | Pekalongan | Kopel | [5 empty] | Boolean | ADD `` TEXT NOT NULL AFTER ``, |  |  |  | "", //
50 | Pekalongan | Kopel | [5 empty] | Boolean | ADD `` TEXT NOT NULL AFTER ``, |  |  |  | "", //
51 | Pekalongan | Kopel | [5 empty] | Boolean | ADD `` TEXT NOT NULL AFTER ``, |  |  |  | "", //
52 | Pekalongan | Kopel | [5 empty] | Boolean | ADD `` TEXT NOT NULL AFTER ``, |  |  |  | "", //
53 | Pekalongan | Kopel | [5 empty] | Boolean | ADD `` TEXT NOT NULL AFTER ``, |  |  |  | "", //
54 |  | Kopel
55 |  | Kopel
56
57
58
59 | [8 empty] | =?,
60
61 | [8 empty] | BCU_BCU_BCPL_FAIL=?,
62 | [8 empty] | BCU_ETHERNET_BCPL_FAIL=?,
BCU_SF6_SF6 STAGE 2 BLOCK=?,
BCU_SF6_STAGE_1_ALARM=?,
BCU_CLOSE_SPRING_UNCHARGE=?,
BCU_MOTOR_MCB_TRIP=?,
BCU_DS_Q1_MOTOR_MCB_TRIP=?,
BCU_DS_Q1_CONTROL_MCB_TRIP=?,
BCU_DS_Q2_MOTOR_MCB_TRIP=?,
BCU_DS_Q2_CONTROL_MCB_TRIP=?,
BCU_B07.BI_13=?,
BCU_F51_FAIL=?,
BCU_F51_ALARM=?,
BCU_TCS_1_FAIL=?,
BCU_TCS_2_FAIL=?,
BCU_PROT_SUPPLY_FAIL=?,
BCU_CONTROL_1_SUPPLY_FAIL=?,
BCU_CONTROL_2_SUPPLY_FAIL=?,
BCU_B07.BI_10=?,
BCU_B07.BI_11=?,
BCU_B07.BI_12=?,
F51_50/51P3.Op=?,
F51_50/51G3.Op=?,
KOSONG=?,
KOSONG=?,
KOSONG=?,
BCU_DS_Q1_DPOS=?,
BCU_DS_Q2_DPOS=?,
BCU_CB_Q0.2_DPOS=?,
=?,
=?,
=?,
=?,
=?,
=?,
=?,
=?,
=?,
=?,
=?,
=?,
=?,
=?,
=?,
=?,
=?,
=?,
=?,
=?,
=?,
=?,
=?,
=?,